## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LD-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0797 |  |  | Transmital Date: 10 Apr 2022
Document Title: Control System Logic Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0797 |  |  | Transmital Date: 10 Apr 2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-IN-LD-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اينكه مدارك پيش نياز هنوز نهايي نشده است و داراي كامنت مي باشد. در طول مهندسي تفصيلي نهايي خواهد شد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | ملاحظه گردید.
2 | با توجه به ماهيت مدرك، مسئوليت صحت عملكرد و تمامي لاجيك ها بر عهده پيمانكار مي باشد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | ملاحظه گردید.
3 | يك جدول در خصوص تگ هاي بكار رفته در اين مدرك اضافه گردد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | در قسمت function/logic به تگ ها و تعداد آن بصورت A/B/C/D/E/F اشاره شده است و نیازی به آوردن جدول تگ ها نمی باشد.
4 | در صفحه 11 در خصوص آيتم Logical 1 كه بصورت (Always 1) در نظر گرفته شده است در قالب يك نوت اضافه گردد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | در صفحه ای 11 به دلیل حذف سیگنال DCS به شیر سولونید یعنی psov ،آيتم Logical 1 كه بصورت (Always 1) می باشد، حذف گردیده است.
5 | با توجه به مذاكرات انجام شده و نا مشخص بودن لوپ FCV لطفا در اين خصوص تاييد كارفرما اخذ گردد. (لاجيك ارائه شده براي اين مورد قابل بررسي نمي باشد) |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | سیگنال کنترلی سطح cascade یعنی LIC مطابق با HAZOP Recommendation Report (بند 135) حذف گردید.
6 | در صفححه 15، در خصوص نمايش Manual/Auto در HMI شفاف سازي صورت پذيرد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | سیگنال کنترلی manual/auto به صورت فرمان در HMI می باشد و status آن در mcc دیده نمی شود . این سیگنال بصورت software در logic دیده شده و در نسخه جدید P&ID ، سیگنال وضعیت manual/auto حذف میگردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 1 May 2022 |  |  |  |  | Date: