## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | LI | 0004 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | AUG.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708005
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for COMPANY Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | LI | 0004 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90 | [6 empty] | CLIENT Approval
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض عمومی و مشترک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 5
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | LI |  | 0004 | D00
REFERENCES:
| F&G LOCATION LAYOUT - EXTENSION OF BINAK BC MANIFOLD | [7 empty] | BK-W007S-PEDCO-110-IN-PY-0005
ABBREVIATIONS:
| I/O | INPUT / OUTPUT | [5 empty] | DCS: |  | DISTRIBUTED CONTROL SYSTEM
| DI: | DIGITAL INPUT SIGNAL | [5 empty] | ESD: |  | EMERGENCY SHUT DOWN SYSTEM
| DO: | DIGITAL OUTPUT SIGNAL | [5 empty] | F&G |  | FIRE AND GAS CONTROL SYSTEM
| AI: | ANALOGUE INPUT SIGNAL | [5 empty] | MCC: |  | MOTOR CONTROL CENTER
| AO: | ANALOGUE OUTPUT SIGNAL | [5 empty] | IRP: |  | INTERPOSING RELAY PANEL
| IND: | INDICATION | [5 empty] | CH: |  | CHANNEL
| STA: | STATUS | [5 empty] | ADD: |  | ADDRESS
| COM: | COMMAND | [5 empty] | TB: |  | TERMINAL BLOCK
| IS: | INTRINSICALLY SAFE | [5 empty] | R: |  | REDUNDANT
| NIS: | NON INTRINSICALLY SAFE | [5 empty] | NR: |  | NON-REDUNDANT
| MAC: | MANUAL CALL POINT | [5 empty] | BR: |  | BLUE BEACON
| HN: | HORN | [5 empty] | BB: |  | RED BEACON
| LHD: | LINEAER HEAT DETECTOR | [5 empty] | FGD: |  | FLAMMABLE GAS DETECTOR
| SD: | SMOKE DETECTOR | [5 empty] | TGD: |  | TOXIC GAS DETECTOR
| BL: | BELL | [5 empty] | FD: |  | FLAME DETECTOR
| FACP: | FIRE ALARM CONTROL PANEL | [5 empty] | IRP: |  | INTERFACE RELAY PANEL
NOTE 1 : |  | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
NOTE 2 : |  | DETAIL INFORMATION OF SYSTEM CABINETS AND MARSHALLING CABINETS INCLUDING: CABINET NAME, RACK AND SLOT NUMBERS, NUMBER OF CHANNELS, ADDRESS OF I/O SIGNALS, TERMINAL BLOCK STRIP NAMES, WHICH ARE SHOWN WITH “*” NOW, WILL BE COMPLETED IN CONTROL SYSTEM VENDORS DOCUMENTS.

## SUMMARY
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O LIST FOR F&G SYSTEMS - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 5
9184 – 073 - 053 |  |  |  | BK | W007S |  | PEDCO | 110 | IN | LI | 0004 | D00
F&G I/O SUMMERY COUNT
CONVENTIONAL
| ITEM | I/O TYPE | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 | AI-NIS-NR | NIS | NR |  | ANALOGUE INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON REDUNDANT) | [6 empty] | 1 |  | 2
| 2 | DI-NIS-NR | NIS | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON REDUNDANT) | [6 empty] | 1 |  | 2
ADDRESSABLE
| ITEM | I/O TYPE | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 | LOOP 1 | - | - |  | 8 IP | [6 empty] | - |  | - | -
| 2 | LOOP 2 | - | - |  | 7 IP | [6 empty] | - |  | -

## IO List for FACP
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
I/O List For F&G System - Extension of Binak B/C Manifold
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 5
9184 – 073 - 053 |  |  |  | BK | W007S | PEDCO | 110 | IN | LI | 0004 | D00
SIGNALS TO FACP
ITEM | TAG | DESCRIPTION | LOCATION | P&ID | SIGNAL TYPE/ Area CLASSIFICATION | I/O TYPE | FROM | TO | POWER SUPPLY | Cable Type | Marshalling Cabinet |  |  | ALARM |  |  |  | REMARK | REV.
[11 empty] | CABINET NO. | TB NO. | ADD. | HH | H | L | LL
FOR CONTROL BUILDING
1 | FACP | Output Port of Loop 1 | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | FACP | MAC-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | -
2 | MAC-2101 | Manual Call Ponit | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2101 | BL-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | -
3 | BL-2101 | Bell | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | BL-2101 | SD-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | -
4 | SD-2101 | Smoke Detector | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2101 | SD-2103 | 24 VDC | By Vendor | - | - | - | - | - | - | -
5 | SD-2103 | Smoke Detector | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2103 | SD-2104 | 24 VDC | By Vendor | - | - | - | - | - | - | -
6 | SD-2104 | Smoke Detector | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2104 | SD-2102 | 24 VDC | By Vendor | - | - | - | - | - | - | -
7 | SD-2102 | Smoke Detector | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2102 | MAC-2104 | 24 VDC | By Vendor | - | - | - | - | - | - | -
8 | MAC-2104 | Manual Call Ponit | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2104 | FACP | 24 VDC | By Vendor | - | - | - | - | - | - | -
9 | FACP | Output Port of Loop 2 | Control Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | FACP | MAC-2102 | 24 VDC | By Vendor | - | - | - | - | - | - | -
10 | MAC-2102 | Manual Call Ponit | WareHouse | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2102 | SD-2107 | 24 VDC | By Vendor | - | - | - | - | - | - | -
11 | SD-2107 | Smoke Detector | WareHouse | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2107 | SD-2105 | 24 VDC | By Vendor | - | - | - | - | - | - | -
12 | SD-2105 | Smoke Detector | Locker Room | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2105 | HD-2101 | 24 VDC | By Vendor | - | - | - | - | - | - | -
13 | HD-2101 | Heat Detector | Kitchen | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | HD-2101 | SD-2106 | 24 VDC | By Vendor | - | - | - | - | - | - | -
14 | SD-2106 | Smoke Detector | WareHouse | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | SD-2106 | MAC-2105 | 24 VDC | By Vendor | - | - | - | - | - | - | -
15 | MAC-2105 | Manual Call Ponit | WareHouse | BK-W007S-PEDCO-110-IN-PY-0005 | Safe Area | Addressable | MAC-2105 | FACP | 24 VDC | By Vendor | - | - | - | - | - | - | -
16 | MAC-2103 | Manual Call Ponit | Existing Charger & Battery room | BK-W007S-PEDCO-110-IN-PY-0005 | Eexd Zone2, IIB T4 | DI-NIS-NR | MAC-2103 | FACP | - | 2 Core x 1.5 | - | - | - | - | - | - | -
17 | HGD-2101 | H2 Gas Detector | Existing Charger & Battery room | BK-W007S-PEDCO-110-IN-PY-0005 | Eexd Zone2, IIB T4 | AI-NIS-NR | HGD-2101 | FACP | 4-20 mA | 3 Core x 1.5 | - | - | - | - | - | - | -
CLIENT Approval
CLIENT Doc. Number: F0Z-708005