## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-DT-0004_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0844 |  |  | Transmital Date: 19-Apr-2022
Document Title: Data Sheets For Diesel Generator of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0844 |  |  | Transmital Date: 19-Apr-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-DT-0004_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ردیف های 2.15 و 2.16 بر مبنای مدرک سایزینگ دیزل ژنراتور و بر اساس آخرین ویریاش مدرک لیست بار اصلاح و به روزرسانی گردند |  | 1401-2294-66366 | 1401-02-28 | این ردیفها بر اساس محاسبات جدید به روز رسانی شدند.
2 | ردیف های 2.21 و 2.22 نوع و تعداد باتری بر اساس باتری نوع H Typeو به صورت نیکل کادمیوم اصلاح شود.. |  | 1401-2294-66366 | 1401-02-28 | اصلاح گردید.
3 | ردیف 9.3 بر مبنای مدرک سایزینگ دیزل ژنراتور و در صورت اصلاح آن به روز گردند. |  | 1401-2294-66366 | 1401-02-28 | اصلاح گردید.
4 | ردیف 9.7 بر مبنای مدرک سایزینگ دیزل محاسبه و مقدارگذاری گردد. |  | 1401-2294-66366 | 1401-02-28 | اصلاح گردید.
5 | ردیف 9.39 تغییرات ولتاژ به 5 درصد افزایش یابد. |  | 1401-2294-66366 | 1401-02-28 | اصلاح گردید.
6 | ردیف 10.15 بر مبنای استاندارد و مدارک مشخصات فنی پروژه تنظیم گردد. |  | 1401-2294-66366 | 1401-02-28 | اصلاح گردید.
7 | ردیف 10.17 حفاظتهای 51 G و 64R قید گردد. |  | 1401-2294-66366 | 1401-02-28 | اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Apr-2022 |  |  |  |  | Date: