## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0002-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0957 |  |  | Transmital Date: 16-May-2022
Document Title: LV Switchgear/MCC Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0957 |  |  | Transmital Date: 16-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-SL-0002-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت فیدر های موتوری بالای 30KW از رله MPR استفاده شود |  | 1400-2294-99024 | 1401-03-22 | مطابق با کامنت آن کارفرمای محترم به شماره نامه 92391 مورخ 25-02-1401 بر روی مدرک اسکماتیک تابلوهای LV، رله MPR اضافه گردید.
2 | کلیه موارد مطرح شده در ارتباط با وضعیت نرمال و یا اضطراری بودن بارها و همچنین موارد مربوطه به سیستم HVACکلید خانه بر اساس کامنت های این امور بر مدرک در Electrical Lod List در این مدرک نیز اعمال گردد. |  | 1400-2294-99024 | 1401-03-22 | بر اساس طراحی سیستم HVAC این مهندسین مشاور برای ساختمان سوییچگیر، فیدرهای Split در نظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: