## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-SL-0002-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0957 |  |  | Transmital Date: 16-May-2022
Document Title: LV Switchgear/MCC Single Line Diagram |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0957 |  |  | Transmital Date: 16-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-SL-0002-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and isuued as AFD after finalizing or minor comments on following documents and below mentioned comments: -Electrical Load List -Calculation note for capacitor bank -Electrical Power & Control Cable Schedule Cable size, type and tag shall be added and specified for all incoming and outgoing feeders base on latest cable sizing and cable schedule. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | در هر زمان از پروژه که تغییراتی در لیست بار برق توسط بخش فرآیند به وجود آید، این مدرک به روزرسانی خواهد شد. بعد از نهایی شدن محاسبات کابل، سایز کابل در این مدرک نشان داده می شود. |  |  | Will be checked later.
2 | There is conflict between this document and electrical typical schematic diagrams For LV panel such as Metering&Protection, Switch fuse, etc . (The document need to match) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | مدرک اسکماتیک و تک خطی هردو به روزرسانی شده و ارسال می گردند. |  |  | Noted and Closed.
3 | Spare feeder shall be considered base on used feeders in single line diagram from point of view size and type. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | فیدرهای Spare اصلاح می گردد. |  |  | See below item 21.
4 | According to our telephone conversation the rated current of main bus bar shall be considered 2000A instead of 1600A (Base on basic single line diagram). |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | بر اساس مدارک پایه به 2000 تغییر پیدا کرد. |  |  | Noted and Closed.
5 | Short circuit time withstand current for diesel generator LV switchgear shall be modified to 1S. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید |  |  | Noted and Closed.
6 | According to Electrical Systems Design Criteria 27/27R, 50BF shall be considered for incomings and bus tie. Meanwhile it shall be mentioned that when function 27 is activated, all outgoing feeders shall be tripped. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | به وسیله یک نوت اضافه گردید. |  |  | See below item 22.
7 | Status to DCS shall be shown for bus tie, all incomings and outgoing motor type feeders. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | همانطور که در مدرک اسکماتیک نشان داده شده است، تمامی سیگنالهای فیدرهای موتوری توسط IRP به DCS فرستاده می شود و نیز مدارک تک خطی و اسکماتیک در مراجع یکدیگر درج شده اند. همچنین نوت شماره 9 جهت ایجاد ارتباط بین ورودی و کوپلر با سیستم dcs اضافه گردید. |  |  | Noted and Closed.
8 | Electrical Interlock with upstream shall be shown. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | در کنار ترانسهای ورودی، "INTERTRIP FROM 11kV SWGR " و "INTERTRIP TO 11kV SWGR " نشان داده شده است. |  |  | See below item 23.
9 | Size of capacitor banks shall be modified base on comments on Calculation note for capacitor bank (especially NISOC comments.) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | مطابق با آخرین محاسبات بانک خازنی و بر اساس ترنسمیتال 590، ظرفیت بانک خازنی 120 کیلووار است که در مدرک در نظر گرفته شده است. در صورت هرگونه تغییر در لیست بار و اضافه شدن توان بیشتر، این مدرک مورد بازنگری قرار خواهد گرفت. |  |  | Noted and Closed.
10 | Current and voltage fualt signal lamp shall be considered separately. Meanwhile all signal lamps descriptions shall be added. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | این بند به صورت یک نوت در مدرک اضافه گردید. |  |  | Noted and Closed.
11 | Number of current transformer for capacitor bank shall be specified. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | عدد یک برای CT بانک خازنی اضافه گردید. چراکه این CT برروی فاز وسط قرار میگیرد. |  |  | Noted and Closed.
12 | Voltage sample for capacitor bank shall be shown.Tag of Capacitor bank (A or B) shall be specified too. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید. |  |  | Noted and Closed.
13 | Emergency stop and start pushbutton shall be considered for all incoming and outgoing feeders on front of switchgear. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | برای فیدرهای خروجی موتوری استارت از طریق LCS و ریموت وجود دارد. در حالیکه STOP از همه جا از جملع درب فیدرامکان پذیر است. برای فیدرهای خروجی غیرموتوری نیز کلید MCCB وجود دارد که استارت و استاپ از طریق چرخش سوییپ نصب شده بر روی درب تابلو مهیا خواهد بود. اسکماتیک استارت و استاپ در مدرک "BK-GCS-PEDCO-120-EL-DG-0002' نشان داده شده است. در مورد فیدرهای ورودی و کوپلر (ACB) نیز نوت 10 اضافه گردید. این نوت در مدرک اسکماتیک نیز اشاره شده است. |  |  | See below item 24.
14 | 400/230V isolating transformer shall be considered separately for each cell. (As sample format) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | نوت شماره 11 به مدرک اضافه گردید. |  |  | Noted and Closed.
15 | Phase Sequence or Phase Balance Relay (47) shall be added for motor starters 18.5kW and above. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | همانطور که در مدرک اسکماتیک نشان داده شده است، تیپ فیدر M3 که برای موتورهای بالاتر از 18.5 کیلووات می باشد، دارای رلهMPR است. |  |  | See below item 25.
16 | Following items shall be added or modified in SLD: |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09
16-1 | 74TCS and other current protection shall be considered in integrated protection unit and then shall be connected to 86 lock out relay. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | برای تمام ورودیها و کوپلرها در نظر گرفته شد. |  |  | Noted and Closed.
16-2 | Alarm window and related note shall be added. (This note shall be added: Alarm window shall be equiped with acknowledge and reset button.) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید. |  |  | Noted and Closed.
16-3 | Type of connection (Hardwire/Serial Link) between measuring unit and DCS shall be shown. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | Serial Link در نظر گرفته شده است. |  |  | Noted and Closed.
16-4 | Selector switch of incomings and bus bars shall be able to show single phase voltage (added as note) |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | به صورت یک نوت اضافه گردید. |  |  | Noted and Closed.
16-5 | According to our agrrement, Switchgear tag shall be added. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید |  |  | Noted and Closed.
16-6 | Frequency added in measuring unit |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید |  |  | Noted and Closed.
17 | Feeder category shall be checked and modified in table for example Feeder category for main compressor carn (CR-101) and Fire Water Pumps cran (CR-014) shall be modified to F1. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | فیدربندی خروجی ها بر اساس مدرک لیست بار به روزرسانی گردید. |  |  | Noted and Closed.
18 | NDP-2101B and NDP-2101C on BUSB shall be clarify (Trere are not in load list). |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | فیدربندی خروجی ها بر اساس مدرک لیست بار به روزرسانی گردید. |  |  | Noted and Closed.
19 | According to IPS-M-EL-143, clause 9.6.3: The heaters shall be fed from dedicated power supply. This power supply system may be energized from a dedicated heater panel, independent distribution panel. The panels feeding the heaters in one section of the switchgear shall be fed from the opposite section of the bus bar. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | مطابق با در ردیف 72 از مدرک لیست بار فیدر SPH-01 & SPH-02 برای این منظور در نظر گرفته شده است. |  |  | Noted and Closed.
20 | Complementry comments will be submitted after receive prerequisit and revised document. |  | BK-SUR-ENG-ELE-00-02611 | 2022-01-09 | اعمال گردید.. |  |  | Noted and Closed.
21 | Re. item 3 above: The number of 40A Motor spare feeder, type M3 on bus A shall be modified. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | با توجه به تغییرات تیپ های موتوری، مدرک اصلاح گردید. |  |  | See below item 29.
22 | Re. item 6 above: According to previous comment, 27R shall be considered for incomings and bus tie. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید.. |  |  | Noted and Closed.
23 | Re. item 8 above: Electrical Interlock (Mechanical/Electrical) with upstream shall be shown. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید.. |  |  | Noted and Closed.
24 | Re. item 13 above: According to our telephone conversation, emergency stop and start (Only for test) pushbutton shall be considered for motor outgoing feeder and MCCB type outgoing feeder equiped with rotary switch (For MCCB type added as note to considered in vendor document.) |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | برای فیدر های موتوری شستی استوپ اضطراری اضافه گردید همچنین rotary switch در نوت 14 اضافه گردید. |  |  | See below item 30.
25 | Re. item 15 above: Phase Sequence or Phase Balance Relay (47) shall be added for motor starters 18.5kW and above. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | با توجه به تغییرات تیپ های موتوری، مدرک اصلاح گردید. |  |  | See below item 31.
26 | According to our telephone conversation the connection between measuring unit and DCS will be serial link, but on pages 8 and 13 has been considered transducer. It shall be modify. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | پیرو تماس تلفنی ارتباط سریال لینک و آنالوگ دستگاه اندازه گیری به DCS در نظر گرفته شد. |  |  | Noted and Closed.
27 | According to our telephone conversation, mechanical transformer protections (63,71,26) shall be connected to Seperat lock out relay (Flagged and Locked Send&Receive Relay ) in LV switchgear. |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید. |  |  | Noted and Closed.
28 | According to our telephone conversation status of DGCB and related incoming LV switchgear shall be modified. (If Required) |  | BK-SUR-ENG-ELE-01-03999 | 2022-04-20 | اعمال گردید. |  |  | Noted and Closed.
29 | Re. item 21 above: Following items shall be rechecked and modified: |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | موارد اعمال می گردد.
29-1 | 8 No. type M3 feeders will be fed by BUS A, but only one spare feeders has been considered on BUS A. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | اضافه گردید.
29-2 | Slug Pump B on bus B shall be modified to type M4, instead of type M3. Meanhwile in spare feeder electronic overload relay shall be considered instead of direct overload relay. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | با توجه به توافقات صورت گرفته از MPR به جای بی متال الکترونیکی برای فیدرهای تیپ M4 لحاظ گردید.
29-3 | Feeder 7 on bus B (LP FLARE PACKAGE) is type F2, so ammeter shall be deleted. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | با توجه به کلید 50 آمپر تیپ فیدر به F1 تغییر یافت.
29-4 | Spare feeder for HVAC PANEL FOR CONTROL ROOM (400A, Type F3) and FIRE WATER JOCKY PUMP (20KW, TYPE 2) shall be added on emergency bus. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | اعمال گردید.
30 | According to our telephone conversation, in addition to shematic diagram document, emergency stop and start (Only for test) pushbutton shall be shown for motor outgoing feeders. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | مطابق با مدرک اسکماتیک، پوش باتون استارت فقط برای حالت تست و پوش باتتون استاپ قارچی در نظر کرفته شده است
31 | According to our telephone conversation, base on note 2, Phase Sequence or Phase Balance Relay (47) shall be added for all motor starters 18.5kW and above. |  | BK-SUR-ENG-ELE-01-04466 | 2022-05-29 | مطابق با مدرک اسکماتیک اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: