## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-CV-CN-0002 |  |  |  |  | EPC Contractor Tr. No. : BK-HD-PEDCO-T-1173 |  |  | Transmital Date: 20-JUL-2022
Document Title: Calculation Note for offsite flood control system |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-CV-T-1173 |  |  | Transmital Date: 20-JUL-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-CV-CN-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در بخش منابع داخلی مدارک پروژه، مورد ذیل افزوده گردد: Standard Drawing for Culvert & Details |  | 1401-2294-164801 | 1401/5/11 | انجام شد
2 | در بخش هدف-مطالعات هیدرولوژیک و هیدرولیک، براساس اطلاعات کانال پیرامونی سایت کافی نبوده، بلکه شرایط توپوگرافی منطقه منتهی به فضای پیزامونی سایت برای کانال های کنترل سیلاب نیز می بایست مورد بررسی قرار گیرد. (حوضه های B-01 & B-02 & B-03) متن سرفصل 2 اصلاح و تکمیل شود. |  | 1401-2294-164801 | 1401/5/11 | محاسبات کانال ها با در نظر گیری توپوگرافی و کلیه شرایط محیطی و پارامترهای لازم انجام شده است. متن اصلاح شد.
3 | در مسیر پایانی آبراهه های منتهی به GCS و برای ممانعت از آسیب های احتمالی ناشی از سیلاب به ایستگاه، موضوع نیاز/عدم نیاز به احداث سازه های بازدارنده ، شفاف سازی گردد. (در شرح قرارداد اشاره شده است : احداث دیوار بتنی، پیرامون واحد و در محل هایی که جهت جلوگیری از ورود سیلاب به واحد تقویت فشار مورد نیاز است) |  | 1401-2294-164801 | 1401/5/11 | بر اساس محاسبات که در گزارش آمده است دبی سر حوضه مقدار ناچیزی است و نیازی به احداث سازه بازدارنده نیست.
4 | نقشه جانمایی کانال پیرامونی بر روی پلان موقعیت ها -صفحه 17 از 20- با توضیحات و جدول نتیجه محاسبات کانال - صفحه 19 از 20 - همخوانی نداشته و ناقص است. اصلاح شود. |  | 1401-2294-164801 | 1401/5/11 | انجام شد
5 | طراحی کانال به صورت خاکی مورد تایید نیست. کانال پیرامونی تیپ بتنی مد نظر قرار گیرد. |  | 1401-2294-164801 | 1401/5/11 | با توجه به کانال های موجود پیرامون سایت که بصورت خاکی اجرا شده است و هم چنین عدم الزام احداث کانال بتنی در شرح کار، طراحی بصورت خاکی در نظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: