## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0018 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0874 |  |  | Transmital Date: 30 Apr 2022
Document Title: STANDARD DRAWING FOR FIRE HYDRANT PAD |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-CV-TR-0874 |  |  | Transmital Date: 30 Apr 2022
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0018-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در پاسخ به ردیف 4 از Clarification(By EPC Contractor) به آگاهی می‌رساند هدف از جوشکاری و اتصالی تعدادی شاخک(میلگرد) به پایه‌های درون بتن، برای گیرداری بیشتر لوله با بتن بوده و نظرات بخش ایمنی در این باره صائب نخواهد بود. بنابراین توضیحات آن پیمانکار مورد تأیید نیست. لذا اعمال گردد. |  | 01/2294/52735 | 1401/02/18 | با توجه به این موضوع که خط لوله مقابله با آتش مدفون در زمین، از جنس پلی اتیلن می‌باشد و در محل شیرهای آتش‌نشانی نیز سه راهی از جنس پلی اتیلن نصب می‌گردد، همچنین لوله‌ای که به سمت سطح زمین اجرا می‌گردد نیز از جنس پلی اتیلن می‌باشد و اولین فلنج جهت اتصال به تجهیزات، بیرون از سطح زمین است. امکان اتصال بین پد بتنی و لوله مذکور وجود ندارد و پد بتنی نیز با ابعاد کافی زیر تجهیزات احداث می‌گردد.
2 | درج عبارت Undistrubed/Drainage material به معنای مشخصات لایه‌های بکفیل نیست. لذا در پاسخ به ردیف 5 Clarification(By EPC Contractor) ضمن اعلام به عدم اعمال نقطه نظر در مدرک، موضوع تعبیه و ارائه گردد. |  | 01/2294/52735 | 1401/02/18 | اعمال شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: