## NIOEC
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-W007S-PEDCO-110-IN-DG-0009_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0946 |  |  | Transmital Date: 5/14/2022
Document Title: Instrument & F&G Junction Box Termination Diagram - EXTENSION OF BINAK B/C MANIFOLD |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-IN-TR-0946 |  |  | Transmital Date: 5/14/2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-IN-DG-0009_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | لیست مدارک مرجع با توجه به عنوان مدرک اضافه گردد. |  | 01/2294/139957 | 1401/04/23 | درخواست کلرفرمای محترم اعمال گردید
2 | جعبه تقسیم و ترمینال دیاگرام مربوط به تجهیزات F&G نمایش داده شود. |  | 01/2294/139957 | 1401/04/23 | تجهیزات F&G بصورت مستقیم به سیستم FACP متصل شده و از JB استفاده نشده است
3 | سیگنال مربوط به سطح موجود ( LEVEL ) جهت اضافه شدن به سیستم جدید نمایش داده شود. |  | 01/2294/139957 | 1401/04/23 | درخواست کلرفرمای محترم اعمال گردید
4 | سیگنال های مربوط به سلکتور سوئیچ ( مطابق نقشه های PID ) نمایش داده نشده است |  | 01/2294/139957 | 1401/04/23 | مدرک مطابق I/O لیست ( CONTROL SYSTEM , ESD ) تهیه شده و همه سیگتالها در نظر گرفته شده است.لطفا در مورد کامنت مورد نظر بیشتر شفاف سازی گردد
5 | وضعیت بازو بسته ، ESDV ها در سیستم DCS نمایش داده شود. |  | 01/2294/139957 | 1401/04/23 | درخواست کلرفرمای محترم اعمال گردید
6 | سیگنال TOTAL SHOUDOWN , ESD سیستم موجود برای سیستم جدید نمایش داده شود |  | 01/2294/139957 | 1401/04/23 | در مدرک INSTRUMENT /F&G CABLE LIST - EXTENSION OF BINAK B/C MANIFOLD آورده شده است. این سیگنال بین سیستمی بوده و نیازی به JB نمی باشد
7
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 23 Feb 2022 |  |  |  |  | Date: