## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
MTO FOR INSTRUMENT CABLE TRAY/LADDER - W007S & MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 3
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | MT | 0005 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
MTO FOR INSTRUMENT CABLE TRAY/LADDER - W007S & MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | AUG.2022 |  | IFI |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class: 3 |  |  |  | Client Doc. Number:'F8Z-708015
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
MTO FOR INSTRUMENT CABLE TRAY/LADDER - W007S & MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 3
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | MT | 0005 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | [8 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Cable Tray
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
MTO FOR INSTRUMENT CABLE TRAY/LADDER - W007S & MANIFOLD
| شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از 3
| 9038 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | MT | 0005 | D00
Instrument Cable Tray/Ladder
ITEM |  | DESCRIPTION | [8 empty] | Qty. |  | Qty.+20% | UNIT
1 |  | PERFORATED CABLE TRAY, HEAVY DUTY; COMPLETE WITH STRAIGHT CONNECTOR AND S.S. CONE-ROOF BOLTS, NUTS & WASHER AND ALL OTHER REQUIRED FACILITIES,STEEL, HOT DIP GALVANIZED,1.6 mm THICK, 300 mm WIDE, 100 mm HIGH , ,STANDARD LENGTH 3m | [8 empty] | 55 ( 3m) |  | 66 ( 3m) | ITEMS |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0
[15 empty] | 30 | 180 | 70 | 280 | 336 | 112 | 134.4 | 44.8 | 115 | 138
2 |  | COVER FOR CABLE TRAY W200; COMPLETE WITH FASTENING FACILITIES,STEEL, HOT DIP GALVANIZED, | [8 empty] | 55 ( 3m) |  | 66 ( 3m) | ITEMS
3 |  | 90 º VERTICAL ELBOW WITH COVER,STEEL, HOT DIP GALVANIZED,200mm WIDE 300 mm HIGH,1.6 mm THICK | [8 empty] | 8 |  | 10 | ITEMS
4 |  | VERTICAL TEE WITH COVER,STEEL, HOT DIP GALVANIZED,300mm WIDE 100 mm HIGH,1.6 mm THICK | [8 empty] | 6 |  | 8 | ITEMS
5 |  | CONDUIT, THREADED MALE ON BOTH SIDES,RIGID STEEL, HOT DIP GALVANIZED, 2" IN LENGTH OF 6 m | [8 empty] | Note 1 |  | Note 1 | ITEMS
6 |  | CONDUIT, THREADED MALE ON BOTH SIDES,RIGID STEEL, HOT DIP GALVANIZED,1" IN LENGTH OF 6 m | [8 empty] | Note 1 |  | Note 1 | ITEMS
7 |  | CONDUIT END BUSHING (FOR CABLE PROTECTION) ,RIGID STEEL, HOT DIP GALVANIZED, 2" | [8 empty] | Note 1 |  | Note 1 | ITEMS
8 |  | CONDUIT END BUSHING (FOR CABLE PROTECTION) ,RIGID STEEL, HOT DIP GALVANIZED,1" | [8 empty] | Note 1 |  | Note 1 | ITEMS
9 |  | CABLE TRAY BRACKET , SUITABLE FOR TRAY : 300 mm | [8 empty] | Note 1 |  | Note 1 | ITEMS
Note 1 Conduit length and cable tray accessories QTY to be finalized later.

## Sheet1 (hidden)
[20 empty] | x | x | x | x
|  | PIPE IN | PIPE IN SCH | PIPE OUT | PIPE OUT SCH | INSULATION/SPEC | TYPE | SIZE | BODY BONNET MATERIAL | CONNECTION IN | CONNECTION OUT | FLG FACE | ENTRY | NACE | PLUG BALL DISK MATERIAL | STEM MATERIAL | LEAKAGE CLASS | SOLENOID | MANUAL RESET | ACTUATOR TYPE | SPRING FAIL ACTION | TRAVELING TIME | LIMIT SWITCH TAG | NOTE1 | NOTE2
ESDV-10010 | PU-PR-PID-0001 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 6 in | A216, Gr WCB/WCC | 6"/3000# | 6"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10010A , SV-10010B | Yes (SV-10010B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-10010 / ZSO-10010 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10011 | PU-PR-PID-0001 | 8" | Sch. 20 , BE | 8" | Sch. 20 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 8 in | A216, Gr WCB/WCC | 8"/3000# | 8"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10011A , SV-10011B | Yes (SV-10011B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-10011 / ZSO-10011 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10012 | PU-PR-PID-0001 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 6 in | A216, Gr WCB/WCC | 6"/3000# | 6"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10012A , SV-10012B | Yes (SV-10012B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-10012 / ZSO-10012 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10013 | PU-PR-PID-0001 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 6 in | A216, Gr WCB/WCC | 6"/3000# | 6"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10013A , SV-10013B | Yes (SV-10013B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-10013 / ZSO-10013 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10014 | PU-PR-PID-0001 | 4" | Sch. 40 , BE | 4" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 4 in | A216, Gr WCB/WCC | 4"/3000# | 4"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10014A , SV-10014B | Yes (SV-10013B) | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-10014 / ZSO-10014 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10015 | PU-PR-PID-0001 | 4" | Sch. 40 , BE | 4" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 4 in | A216, Gr WCB/WCC | 4"/3000# | 4"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10015A , SV-10015B | Yes (SV-10015B) | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-10015 / ZSO-10015 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10016 | PU-PR-PID-0001 | 4" | Sch. 40 , BE | 4" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 4 in | A216, Gr WCB/WCC | 4"/3000# | 4"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10016A , SV-10016B | Yes (SV-10016B) | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-10016 / ZSO-10016 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10017 | PU-PR-PID-0001 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 6 in | A216, Gr WCB/WCC | 6"/3000# | 6"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10017A , SV-10017B | Yes (SV-10017B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-10017 / ZSO-10017 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10018 | PU-PR-PID-0001 | 4" | Sch. 40 , BE | 4" | Sch. 40 , BE | VN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 4 in | A216, Gr WCB/WCC | 4"/3000# | 4"/3000# | RTJ | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10018A , SV-10018B | Yes (SV-10018B) | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-10018 / ZSO-10018 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-10053 | PU-PR-PID-0002 | 3" | Sch. 40 , BE | 3" | Sch. 40 , BE | CN06 / Painting | Full Bore Ball Valve | 3 in | ASTM A216 WCB | 3"/300# | 3"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10053 | Yes (SV-10053) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-10053 / ZSO-10053 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10084 | PU-PR-PID-0039 | 10" | Sch. 20 , BE | 10" | Sch. 20 , BE | AN01 | Full Bore Ball Valve/Trunnion Mounted | 10 in | ASTM A216 WCB | 10"/300# | 10"/300 | RF | Top Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-10010A , SV-10010B | Yes (SV-10084B) | Single Acting , Spring Return | Fail to Close | 10 Sec. | ZSC-10084 / ZSO-10084 | (1) PMS: Piping material specification
BDV-10093 | PU-PR-PID-0006 | 3" | Sch. 40 , BE | 3" | Sch. 40 , BE | CN06 / Painting | Full Bore Ball Valve | 3 in | ASTM A216 WCB | 3"/300# | 3"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10093 | Yes (SV-10093) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-10093 / ZSO-10093 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-10095 | PU-PR-PID-0006 | 10" | Sch. 20 , BE | 10" | Sch. 20 , BE | CN06 | Full Bore Ball Valve/Trunnion Mounted | 10 in | ASTM A216 WCB | 10"/300# | 10"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-10095A , SV-10095B | Yes (SV-10095B) | Single Acting , Spring Return | Fail to Close | 10 Sec. | ZSC-10095 / ZSO-10095 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-24002 | PU-PR-PID-0013 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN01 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-24002 | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-24002 / ZSO-24002 | (1) PMS: Piping material specification
SDV-23010 | PU-PR-PID-0016 | 4" | Sch. 40 , BE | 4" | Sch. 40 , BE | FN01 / Painting | Full Bore Ball Valve | 4 in | ASTM A216 WCB | 4"/600# | 4"/600# | RF | Top Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-23010 | Yes (SV-23010) | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-23010 / ZSO-23010 | (1) PMS: Piping material specification
XV-23011 | PU-PR-PID-0016 | 1" | Sch. 160 , PE | 1" | Sch. 160 , PE | FN01 / Painting | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/600# | 1"/600# | RF | Side Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-23011 | No | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-23011 / ZSO-23011 | (1) PMS: Piping material specification
ESDV-11010 | PU-PR-PID-0020 | 8" | Sch. 20 , BE | 8" | Sch. 20 , BE | AN04 / Painting | Full Bore Ball Valve | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11010A , SV-11010B | Yes (SV-11010B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11010 / ZSO-11010 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-11011 | PU-PR-PID-0020 | 12" | Sch. 20 , BE | 12" | Sch. 20 , BE | AN03 / Painting | Full Bore Ball Valve | 12 in | ASTM A216 WCB | 12"/300# | 12"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11011A , SV-11011B | Yes (SV-11011B) | Single Acting , Spring Return | Fail to Close | 10 Sec. | ZSC-11011 / ZSO-11011 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-11012 | PU-PR-PID-0020 | 12" | Sch. 20 , BE | 12" | Sch. 20 , BE | AN03 / Painting | Full Bore Ball Valve | 12 in | ASTM A216 WCB | 12"/300# | 12"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11012A , SV-11012B | Yes (SV-11012B) | Single Acting , Spring Return | Fail to Close | 10 Sec. | ZSC-11012 / ZSO-11012 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11013 | PU-PR-PID-0020 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11013A , SV-11013B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11013 / ZSO-11013 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11021 | PU-PR-PID-0021/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11021 | Yes (SV-11021) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11021 / ZSO-11021 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11020 | PU-PR-PID-0021/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11020A , SV-11020B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11020 / ZSO-11020 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11023A | PU-PR-PID-0021/1 | 10" | Sch. 20 , BE | 10" | Sch. 20 , BE | AN04 / Painting | Full Bore Ball Valve | 10 in | ASTM A216 WCB | 10"/300# | 10"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11023A | Yes (SV-11023A) | Single Acting , Spring Return | Fail to Close | 10 Sec. | ZSC-11023A / ZSO-11023A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11025A | PU-PR-PID-0021/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11025A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11025A / ZSO-11025A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11024A | PU-PR-PID-0021/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Insulation for personnel protect. | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11024A | Yes (SV-11024A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11024A / ZSO-11024A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11026A | PU-PR-PID-0021/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11026A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11026A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11027A | PU-PR-PID-0021/1 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11027A | Yes (SV-11027A) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11027A / ZSO-11027A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11028A | PU-PR-PID-0021/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11028A | Yes (SV-11028A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11028A / ZSO-11028A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11023B | PU-PR-PID-0021/2 | 10" | Sch. 20 , BE | 10" | Sch. 20 , BE | AN04 / Painting | Full Bore Ball Valve | 10 in | ASTM A216 WCB | 10"/300# | 10"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11023B | Yes (SV-11023B) | Single Acting , Spring Return | Fail to Close | 10 Sec. | ZSC-11023B / ZSO-11023B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11025B | PU-PR-PID-0021/2 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11025B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11025B / ZSO-11025B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11024B | PU-PR-PID-0021/2 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Insulation for personnel protect. | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11024B | Yes (SV-11024B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11024B / ZSO-11024B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11026B | PU-PR-PID-0021/2 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11026B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11026B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11027B | PU-PR-PID-0021/2 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11027B | Yes (SV-11027B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11027B / ZSO-11027B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11028B | PU-PR-PID-0021/2 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11028B | Yes (SV-11028B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11028B / ZSO-11028B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-11040 | PU-PR-PID-0022 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11040A , SV-11040B | Yes (SV-11040B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11040 / ZSO-11040 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-11042 | PU-PR-PID-0022 | 8" | Sch. 20 , BE | 8" | Sch. 20 , BE | AN04 | Full Bore Ball Valve | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11042A , SV-11042B | Yes (SV-11042B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11042 / ZSO-11042 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11051 | PU-PR-PID-0023/1 | 3" | Sch. 40 , BE | 3" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 3 in | ASTM A216 WCB | 3"/300# | 3"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11051 | Yes (SV-11051) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11051 / ZSO-11051 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11053A | PU-PR-PID-0023/1 | 8" | Sch. 20 , BE | 8" | Sch. 20 , BE | AN04 / Painting | Full Bore Ball Valve | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11053A | Yes (SV-11053A) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11053A / ZSO-11053A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11055A | PU-PR-PID-0023/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11055A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11055A / ZSO-11055A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11054A | PU-PR-PID-0023/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Insulation for personnel protect. | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11054A | Yes (SV-11054A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11054A / ZSO-11054A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11056A | PU-PR-PID-0023/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11056A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11056A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11057A | PU-PR-PID-0023/1 | 6" | Sch. 40 , BE | 6" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11057A | Yes (SV-11057A) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11057A / ZSO-11057A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11058A | PU-PR-PID-0023/1 | 2" | Sch. 40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11058A | Yes (SV-11058A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11058A / ZSO-11058A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11053B | PU-PR-PID-0023/2 | 8" | Sch.20 , BE | 8" | Sch. 20 , BE | AN04 / Painting | Full Bore Ball Valve | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11053B | Yes (SV-11053B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11053B / ZSO-11053B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11055B | PU-PR-PID-0023/2 | 2" | Sch.40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11055B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-10055B / ZSO-11055B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11054B | PU-PR-PID-0023/2 | 2" | Sch.40 , BE | 2" | Sch. 40 , BE | AN04 / Insulation for personnel protect. | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11054B | Yes (SV-11054B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11054B / ZSO-11054B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11056B | PU-PR-PID-0023/2 | 2" | Sch.40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11056B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11056B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11057B | PU-PR-PID-0023/2 | 6" | Sch.40 , BE | 6" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11057B | Yes (SV-11057B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11057B / ZSO-11057B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11058B | PU-PR-PID-0023/2 | 2" | Sch.40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11058B | Yes (SV-11058B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11058B / ZSO-11058B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11071 | PU-PR-PID-0024/1 | 2" | Sch.40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11071 | Yes (SV-11071) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11071 / ZSO-11071 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11073A | PU-PR-PID-0024/1 | 6" | Sch.40 , BE | 6" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11073A | Yes (SV-11073A) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11073A / ZSO-11073A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11075A | PU-PR-PID-0024/1 | 2" | Sch.40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11075A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11075A / ZSO-11075A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11074A | PU-PR-PID-0024/1 | 3" | Sch.40 , BE | 3" | Sch. 40 , BE | CN06 / Insulation for personnel protect. | Full Bore Ball Valve | 3 in | ASTM A216 WCB | 3"/300# | 3"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11074A | Yes (SV-11074A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11074A / ZSO-11074A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11076A | PU-PR-PID-0024/1 | 2" | Sch.80 , BE | 2" | Sch. 80 , BE | CN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11076A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11076A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11077A | PU-PR-PID-0024/1 | 6" | Sch.40 , BE | 6" | Sch. 40 , BE | CN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11077A | Yes (SV-11077A) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11077A / ZSO-11077A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11078A | PU-PR-PID-0024/1 | 2" | Sch.80 , BE | 2" | Sch.80 , BE | CN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11078A | Yes (SV-11078A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11078A / ZSO-11078A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11073B | PU-PR-PID-0024/2 | 6" | Sch.40 , BE | 6" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | 13 % Cr | 13 % Cr | ANSI Class V | SV-11073B | Yes (SV-11073B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11073B / ZSO-11073B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11075B | PU-PR-PID-0024/2 | 2" | Sch.40 , BE | 2" | Sch. 40 , BE | AN04 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11075B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11075B / ZSO-11075B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11074B | PU-PR-PID-0024/2 | 3" | Sch.40 , BE | 3" | Sch. 40 , BE | CN06 / Insulation for personnel protect. | Full Bore Ball Valve | 3 in | ASTM A216 WCB | 3"/300# | 3"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11074B | Yes (SV-11074B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11074B / ZSO-11074B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11076B | PU-PR-PID-0024/2 | 2" | Sch.80 , BE | 2" | Sch. 80 , BE | CN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11076B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11076B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11077B | PU-PR-PID-0024/2 | 6" | Sch.40 , BE | 6" | Sch. 40 , BE | CN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 6 in | ASTM A216 WCB | 6"/300# | 6"/300# | RF | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11077B | Yes (SV-11077B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11077B / ZSO-11077B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11078B | PU-PR-PID-0024/2 | 2" | Sch.80 , BE | 2" | Sch. 80 , BE | CN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11078B | Yes (SV-11078B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11078B / ZSO-11078B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-11091 | PU-PR-PID-0025 | 8" | Sch.20 , BE | 8" | Sch. 20 , BE | CN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11091A , SV-11091B | Yes (SV-11091B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11091 / ZSO-11091 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11101 | PU-PR-PID-0026/1 | 3" | Sch.40 , BE | 3" | Sch. 40 , BE | CN06 / Painting | Full Bore Ball Valve | 3 in | ASTM A216 WCB | 3"/300# | 3"/300# | RF | Side Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11101 | Yes (SV-11101) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11101 / ZSO-11101 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11103A | PU-PR-PID-0026/1 | 8" | Sch.20 , BE | 8" | Sch. 20 , BE | CN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11103A | Yes (SV-11103A) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11103A / ZSO-11103A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11105A | PU-PR-PID-0026/1 | 2" | Sch.80 , BE | 2" | Sch. 80 , BE | CN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11105A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11105A / ZSO-11105A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11104A | PU-PR-PID-0026/1 | 2" | Sch.80 , BE | 2" | Sch. 80 , BE | FN06 / Insulation for personnel protect. | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/600# | 2"/600# | RF | Side Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11104A | Yes (SV-11104A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11104A / ZSO-11104A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11106A | PU-PR-PID-0026/1 | 2" | Sch.80 , BE | 2" | Sch. 80 , BE | FN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/600# | 2"/600# | RF | Side Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11106A | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11106A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11107A | PU-PR-PID-0026/1 | 6" | Sch.80 , BE | 6" | Sch. 80 , BE | FN06 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/600# | 6"/600# | RF | Top Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11107A | Yes (SV-11107A) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11107A / ZSO-11107A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11108A | PU-PR-PID-0026/1 | 2" | Sch.80 , BE | 2" | Sch. 80 , BE | FN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/600# | 2"/600# | RF | Side Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11108A | Yes (SV-11108A) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11108A / ZSO-11108A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11109A | PU-PR-PID-0026/1 | 1" | Sch.XXS , PE | 1" | Sch. XXS , PE | FN06 / Painting | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/600# | 1"/600# | RF | Side Entry | YES | 316L + Stellite 6 | 316L + Stellite 6 - Nace | ANSI Class V | SV-11109AA , SV-11109AB | No | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11109A / ZSO-11109A | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11110 | PU-PR-PID-0026/1 | 1" | Sch 160 , PE | 1" | Sch 160 , PE | CN06 / Painting | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/300# | 1"/300# | RF | Side Entry | YES | 316L + Stellited | AISI 316L -Nace | ANSI Class V | SV-11110A , SV-11110B | No | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11110 / ZSO-11110 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11103B | PU-PR-PID-0026/2 | 8" | Sch.20 , BE | 8" | Sch.20 , BE | CN06 / Painting | Full Bore Ball Valve/Trunnion Mounted | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | Yes | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11103B | Yes (SV-11103B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11103B / ZSO-11103B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11105B | PU-PR-PID-0026/2 | 2" | Sch.80 , BE | 2" | Sch.80 , BE | CN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/300# | 2"/300# | RF | Side Entry | YES | AISI 316 L | AISI 316 L-Nace | ANSI Class V | SV-11105B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11105B / ZSO-11105B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11104B | PU-PR-PID-0026/2 | 2" | Sch.80 , BE | 2" | Sch.80 , BE | FN06 / Insulation for personnel protect. | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/600# | 2"/600# | RF | Side Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11104B | Yes (SV-11104B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11104B / ZSO-11104B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11106B | PU-PR-PID-0026/2 | 2" | Sch.80 , BE | 2" | Sch.80 , BE | FN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/600# | 2"/600# | RF | Side Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11106B | No | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11106B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
SDV-11107B | PU-PR-PID-0026/2 | 6" | Sch.80 , BE | 6" | Sch.80 , BE | FN06 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/600# | 6"/600# | RF | Top Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11107B | Yes (SV-11107B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11107B / ZSO-11107B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11108B | PU-PR-PID-0026/2 | 2" | Sch.80 , BE | 2" | Sch.80 , BE | FN06 / Painting | Full Bore Ball Valve | 2 in | ASTM A216 WCB | 2"/600# | 2"/600# | RF | Side Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11108B | Yes (SV-11108B) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11108B / ZSO-11108B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11109B | PU-PR-PID-0026/2 | 1" | Sch.XXS , PE | 1" | Sch.XXS , PE | FN06 / Painting | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/600# | 1"/600# | RF | Side Entry | YES | 316L + Stellite 6 | 316L + Stellite 6 - Nace | ANSI Class V | SV-11109BB , SV-11109BA | No | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11109B / ZSO-11109B | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11110B | PU-PR-PID-0026/2 | 1" | Sch.XXS , PE | 1" | Sch.XXS , PE | FN06 | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/600# | 1"/600# | RF | Side Entry | YES | 316L + Stellite 6 | 316L + Stellite 6 | ANSI Class V | SV-11110B1 , SV-11110B2 | Yes (SV-11110B2) | Single Acting , Spring Return | Fail to Close | 4 Sec. | ZSC-11110B / ZSO-11110B | (1) PMS: Piping material specification
ESDV-11120 | PU-PR-PID-0027 | 6" | Sch.40 , BE | 6" | Sch.40 , BE | FN01 / Painting | Full Bore Ball Valve | 6 in | ASTM A216 WCB | 6"/600# | 6"/600# | RF | Top Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-11120A , SV-11120B | Yes (SV-11120B) | Single Acting , Spring Return | Fail to Close | 6 Sec. | ZSC-11120 / ZSO-11120 | (1) PMS: Piping material specification
XV-11121 | PU-PR-PID-0027 | 1" | Sch.160 , PE | 1" | Sch.160 , PE | FN01 / Painting | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/600# | 1"/600# | RF | Side Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-11121 | No | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11121 / ZSO-11121 | (1) PMS: Piping material specification
XV-11130 | PU-PR-PID-0028 | 1" | Sch.XXS , PE | 1" | Sch.XXS , PE | FN06 / Painting | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/600# | 1"/600# | RF | Side Entry | YES | 316L + Stellite 6 | 316L + Stellite 6 - Nace | ANSI Class V | SV-11130A , SV-11130B | No | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11130 / ZSO-11130 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
BDV-11132 | PU-PR-PID-0028 | 2 1/2" | Sch.80 , BE | 2 1/2" | Sch.80 , BE | FN06 / Painting | Full Bore Ball Valve | 2 1/2 in | ASTM A216 WCB | 2 1/2"/600# | 2 1/2"/600# | RF | Side Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11132 | Yes (SV-11132) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11132 / ZSO-11132 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-11134 | PU-PR-PID-0028 | 8" | Sch.80 , BE | 8" | Sch.80 , BE | FN06 / Painting | Full Bore Ball Valve | 8 in | ASTM A216 WCB | 8"/600# | 8"/600# | RF | Top Entry | Yes | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11134A , SV-11134B | Yes (SV-11134B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11134 / ZSO-11134 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10150 | PU-PR-PID-0039 | 8" | Sch.40 , BE | 8" | Sch.40 , BE | FN01 / Painting | Full Bore Ball Valve | 8 in | ASTM A216 WCB | 8"/600# | 8"/600# | RF | Top Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-10150A , SV-10150B | Yes (SV-10150B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-10150 / ZSO-10150 | (1) PMS: Piping material specification
ESDV-10151 | PU-PR-PID-0039 | 8" | Sch.20 , BE | 8" | Sch.20 , BE | CN01 / Painting | Full Bore Ball Valve/Trunnion Mounted | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | No | 13 % Cr | 13 % Cr | ANSI Class V | SV-10151A , SV-10151B | Yes (SV-10151B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-10151 / ZSO-10151 | (1) PMS: Piping material specification
SDV-11029 | PU-PR-PID-0021/2 | 3" | Sch.40 , BE | 3" | Sch.40 , BE | AN04 / Painting | Full Bore Ball Valve | 3in | ASTM A216 WCB | 3"/300# | 3"/300# | RF | Side Entry | Yes | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11029 | Yes (SV-11029) | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11029 / ZSO-11029 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-11092 | PU-PR-PID-0025 | 8" | Sch.20 , BE | 8" | Sch.20 , BE | AN04 / Painting | Full Bore Ball Valve | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | YES | 13 % Cr | 13 % Cr-Nace | ANSI Class V | SV-11092A , SV-11092B | Yes (SV-11092B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-11092 / ZSO-11092 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
XV-11135 | PU-PR-PID-0028 | 1" | Sch.XXS , PE | 1" | Sch.XXS , PE | FN06 / Painting | Full Bore Ball Valve | 1 in | ASTM A105 | 1"/600# | 1"/600# | RF | Side Entry | YES | 316L + Stellite 6 | 316L + Stellite 6-Nace | ANSI Class V | SV-11135 | No | Single Acting , Spring Return | Fail to Open | 4 Sec. | ZSC-11135 / ZSO-11135 | (1) All wetted parts shall fully comply with NACE, MR 01-75 (Latest Revision). | (2) PMS: Piping material specification
ESDV-10152 | PU-PR-PID-0039 | 8" | Sch.20 , BE | 8" | Sch.20 , BE | AN01 / Painting | Full Bore Ball Valve/Trunnion Mounted | 8 in | ASTM A216 WCB | 8"/300# | 8"/300# | RF | Top Entry | NO | 13 % Cr | 13 % Cr | ANSI Class V | SV-10152A , SV-10152B | Yes (SV-10152B) | Single Acting , Spring Return | Fail to Close | 8 Sec. | ZSC-10152 / ZSO-10152 | (1) PMS: Piping material specification