## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-BK15-PEDCO-110-EL-MR-0005_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0866 |  |  | Transmital Date: 27-Apr-2022
Document Title: PMR For DC Charger - BK15 |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0866 |  |  | Transmital Date: 27-Apr-2022
[5 empty] | CRS No: NISOC-CRS-BK-BK15-PEDCO-110-EL-MR-0005_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق با بند 5.1.1 این مدرک و مطابق با شرح پیمان، شارژرهای مربوط به باتری های نیکل کادمیوم دیزل ژنراتور از نوع تایرستوری و صنعتی می باشد. لذا لازم است مشخصات شارژر 24 VDC در جدول بند 2 قید گردد. |  | 1401-2294-78862 | 1401-03-08 | با توجه به اینکه تأمین باتری های دیزل ژنراتور برای استارتینگ در حیطه کاری سازنده می باشد، لذا شارژر مربوط به این باتری ها نیز در خود تابلوی کنترل دیزل توسط ایشان در نظر گرفته می شود. از اینرو عبارت 24 VDC که به اشتباه ذکر گردیده بود، از متن حذف گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 10-May-22 |  |  |  |  | Date: