## Reply Sheet
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-CV-DW-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0448 |  |  | Transmital Date: 11-JAN-2022
Document Title: Standard Drawing For Catch Basins |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-CV-T-0448 |  |  | Transmital Date: 11-JAN-2022
[5 empty] | CRS No:NISOC-CRS-BK-GNRAL-PEDCO-000-CV-DW-0006-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | توضیحات بند چهار از REPLY SHEET مورد تایید نیست. با توجه به اذعان آن پیمانکار مبنی بر عدم امکان انجام تراکم خاک - یک نقص محسوب می شود- پیشنهاد می گردد برای رفع این مهم، عمق خاکبرداری بیشتر گردیده و با حداقل 35 سانتی متر قلوه سنگ کف سازی انجام گردد. |  | 1400-2294-364648 | 1400/10/25 | با 35 سانتی متر قلوه سنگ کف سازی شد.
2 | نوع سیمان براساس گزارش ژئوتکنیک تعیین و درج شده است؟ در NOTES اشاره شود که پس از تصویب گزارش مکانیک خاک تیپ سیمان اعلام خواهد شد. |  | 1400-2294-364648 | 1400/10/25 | اعمال شد
3 | سایز تمامی آرماتور های کف، بدنه و سقف به Ø12 بازگردانده شود. |  | 1400-2294-364648 | 1400/10/25 | اعمال شد
4 | در توضیحات PIT DIMENSION به تیپ آرماتور در حالت های مختلف اشاره شده که طبق بند سه اصلاح گردد. |  | 1400-2294-364648 | 1400/10/25 | اعمال شد
5 | نحوه آب بند شدن سازه با اتصال STEEL PLATE به دیواره بتنی توضیح داده شود. |  | 1400-2294-364648 | 1400/10/25 | اعمال شد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: