## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-LI-0001-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0692 |  |  | Transmital Date: 07-Mar-2022
Document Title: Electrical Load List - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-0692 |  |  | Transmital Date: 07-Mar-2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-EL-LI-0001-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | صفحه 3 از 5 تقسیم بندی فیدرهای و استارترها بر اساس محدوده توانی استاندارد IPS-E-EL-100(1) اصلاح گردد |  | 1401-2294-1235 | 1401-01-06 | مطابق با آخرین ویرایش از مدرک Electrical Load List ارسال شده با ترنسمیتال 1193، تقسیم بندی فیدرها و استارترها به روزرسانی گردید.
2 | توان در نظر گرفته شده برای فیدرهای UPS و شارژر بر اساس محاسبات نهایی این سیستمها بازنگری قرار گیرد. |  | 1401-2294-1235 | 1401-01-06 | توانهای مورد نیاز سیستم AC UPS و باتری شارژر بر اساس آخرین ویرایش بارهای ابزاردقیق ارسال شده در ترنسمیتال 852 در نظر گرفته شده است. در صورت تغییر در لیست بار ابزاردقیق این مدرک به روزرسانی خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 15-Mar-22 |  |  |  |  | Date: