## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR LEVEL TRANSMITTER - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | DT | 0012 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR LEVEL TRANSMITTER - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | AUG.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | DEC.2021 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-707982
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved
D02

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR LEVEL TRANSMITTER - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از5
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | DT | 0012 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128
D02

## Reference
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR LEVEL TRANSMITTER - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از5
9184 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | DT | 0012 | D02
REFERENCE DOCUMENTS :
| Specification For Instrumentation | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| Process Basis Of Design | [5 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| P&ID - Extension of Binak B/C Manifold | [5 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| Piping Material Specification | [5 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
| Instrument & Control System Design Criteria | [5 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
| Process Flow Diagram - Extension of Binak B/C Manifold | [5 empty] | BK-W007S-PEDCO-110-PR-PF-0001
| Instrument Hook-up Diagram - Extension of Binak B/C Manifold | [5 empty] | BK-W007S-PEDCO-110-IN-DG-0003
D02

## Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR LEVEL TRANSMITTER - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از5
9184 – 073 - 053 |  |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0012 | D02
GENERAL NOTES:
1- Wetted part shall be in according To NACE MR-0175/ISO 15156 .
2- The torque tube connection with the chamber shall be flanged.
3- The torque tube connection with the chamber shall be flanged.
4- All transmitters shall be equipped with internal diagnostics software
5- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
6- A material certificate to EN 10204: 2004 type 3.1 shall be provided for each process wetted part.
7- Any pressure bearing welds shall be subject to 100% radiography inspection by qualified welding NDT inspectors.
8- All transmitters shall have output short circuit & reverse polarity protection.
9- The transmitter digital electronics shall have a non-volatile EEPROM memory to be used for storing the configuration data and sensor
10- Material Test Certificates and Calibration shall submit for each level Transmitter by vendor.
11- Sunshade to be considered for all electronic parts.
12- An internal stilling well should be supplied by VENDOR, and have an internal diameter of at least 25 mm larger than the diameter for internal type displacer.
13- Environmental Condition For Field Instrumentation Of Binak Oilfield Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: -5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % (Note */ Note**) DB FOR Winter HVAC Design: 6 °C Note * * Refer to " HVAC Design Criteria; N.I.O.C. NO.: F-1-B-422001". ** Refer to “NISOC Meteorological Studies Report".
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
D02

## LT-1701
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR LEVEL TRANSMITTER - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 5 از 5
9184 – 073 - 053 | [5 empty] | BK | W007S | PEDCO |  | 110 | IN | DT |  | 0012 | D02
DATA SHEETS FOR LEVEL TRANSMITTER ( TYPE)
GENERAL |  | 1 | Tag Number | [9 empty] | LT-1701
|  | 2 | Service | [9 empty] | OIL SUMP PUMP
|  | 3 | Location | [9 empty] | P-1701
|  | 4 | Mounting Type | [9 empty] | Internal
|  | 5 | Application | [9 empty] | Level Control
|  | 6 | P&ID No. | [9 empty] | BK-W007S-PEDCO-110-PR-PI-0001 (6/6)
PROCESS CONDITIONS |  | 7 | Upper Liquid \ vapor | [9 empty] | Oil \ vapor
|  | 8 | Lower Liquid | [9 empty] | Not applicable
|  | 9 | Density Lower | Density Upper |  |  |  |  | Density Upper \ vapor |  |  |  | Not applicable |  |  |  | 850.2 Kg/m3 \ 10.00 Kg/m3
|  | 10 | Design Pressure | Normal Pressure |  |  |  |  | Normal Pressure |  |  |  | ATM+FULL OF WATER |  |  |  | ATM
|  | 11 | Design Temp. | Normal Temp. |  |  |  |  | Normal Temp. |  |  |  | 85°C |  |  |  | AMB
|  | 12 | Viscosity Low. | Viscosity Up |  |  |  |  | Viscosity Up \ vapor |  |  |  | Not applicable |  |  |  | 9.69 cp \ 0.011 cp
BODY / GAGE |  | 13 | Body/Cage Material | [9 empty] | N/A
|  | 14 | Body/Cage Rating | [9 empty] | N/A
|  | 15 | Connection Size & Location | [9 empty] | N/A
|  | 16 | - | [9 empty] | N/A
|  | 17 | Flange Material | [9 empty] | N/A
|  | 18 | Length of Center To Center | [9 empty] | N/A
|  | 19 | Case Mounting | [9 empty] | N/A
|  | 20 | Rotatable Head | [9 empty] | N/A
|  | 21 | Orientation | [9 empty] | N/A
|  | 22 | Cooling Extension | [9 empty] | N/A
SENSOR |  | 23 | Sensor Type | [9 empty] | Cable Float
|  | 24 | Sensor Quantity | [9 empty] | 1
|  | 25 | Sensor Dimention | [9 empty] | VTA
|  | 26 | Selected Standard Span | [9 empty] | VTA
|  | 27 | Insertion Depth | [9 empty] | 3000mm
|  | 28 | Rod Material | [9 empty] | S.S. 316L (VTC)
|  | 29 | Float Material | [9 empty] | VTA
|  | 30 | Cable Material | [9 empty] | VTA
|  | 31 | Wetted Part Material | [9 empty] | S.S. 316L (VTC)
TRANSMITTER |  | 32 | Function | [9 empty] | Level Transmitter
|  | 33 | Output | [9 empty] | 4~20mA, SMART HART
|  | 34 | Set Range |  |  | Min. |  |  | Max. |  |  |  | 0 |  |  |  | 100%
|  | 35 | Ingress Protection | [9 empty] | IP65
|  | 36 | Mounting Location | [9 empty] | Top Mounted
|  | 37 | Connection Size & Location | [9 empty] | 4" , Plate mounted (Note 1)
|  | 38 | Ex Protection | [9 empty] | Zone 2, EEx ia IIB T4
|  | 39 | Power Supply | [5 empty] | Cable Entry |  |  |  | 24 VDC, loop powered |  |  |  | M20x1.5
|  | 40 | Accuracy | [9 empty] | 0.1% of full scale
|  | 41 | Integral Indicator | [9 empty] | Digital LCD
|  | 42 | Zero/Span Adjusment | [9 empty] | VTA
|  | 43 | Termination Type | [9 empty] | Screw terminal
|  | 44 | Case Material | [9 empty] | die-cast aluminum
OPTIONS |  | 45 | Cable Gland | [9 empty] | M20x1.5 , EExd
|  | 46 | Vent/Drain Connection | [9 empty] | N/A
|  | 47 | - | [9 empty] | -
|  | 48 | Custom Tag | [9 empty] | S.S. permanent attached
PURCHASE |  | 49 | Manufacturer | [9 empty] | Will be finalized later
|  | 50 | Model | [9 empty] | Will be finalized later
Notes:
| VTA: Vendor to Advice |  |  |  | VTC: Vendor to Confirm
1- Mounted on a plate as per Project Hook- up diagram (Required plate and accessories for connect to concrete wall of sump to be supplied by Civil department.)
D02