## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 10
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | DT | 0005 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | AUG.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-707975
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 10
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | DT | 0005 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X |  | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 | X | X | X | [5 empty] | 73
10 | X | X | X | [5 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 10
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT |  | 0005 | D02
REFERENCE DOCUMENTS :
| 1. | Specification for Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| 2. | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 3. | P&ID - Extension of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| 4. | Piping Material Specification | [6 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
| 5. | Instrument & Control System Design Criteria | [6 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
| 6. | Process Flow Diagram - Extension of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-PR-PF-0001
| 7. | Specification for ON OFF / Shutdown Valves | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0006
| 8. | Instrument Hook-up Diagram - Extension of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-IN-DG-0003

## Note
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 10
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0005 | D02
GENERAL NOTES:
1. Calculations shall be provided for each completely piped actuated valve assembly (including solenoid valve), the stroking times i.e. to close and to open.
2. The duty, failure action and stroke time shall all be approved by the Purchaser.
3. The actuator shall be designed to operate the valve through its full stroke.
4. The maximum valve stroking time to achieve the safety position shall be defined according to size of the body (5 seconds for body until 4", 1 second per inch for body greater than 4").
5. The piping indicates corrosion allowance selected as per document "PIPELINE MATERIAL SPECIFICATION, No. " BK-SSGRL-PEDCO-110-PL-SP-0001 " :
6. Hydro-test duration shall be in accordance with API 6D.
7. All ball valves shall be fitted with suitable 'end of travel' stops at the fully open and fully closed positions and a local position indicator. The design shall prevent the ingress of foreign material and corrosion products which would impair the operation of the stops. Devices capable of locking the valves in their safe position (ESDV in open or closed position) shall be provided for maintenance and shall be vendor's standard proven design.
8. Vendor shall guarantee and demonstrate the required stroking speed, during the Functional Test (FAT).
9. A manual hand valve shall be provided in pneumatic control system in order to bypass the solenoid valves. So, the valves could be open and closed using this manual valve by pressurizing and depressurizing the pneumatic line. The facilities shall be provided in order to lock and unlock this manual valve using a special key.
10. All accessories shall be mounted, together with solenoid valve, etc., on a 316SS sub-plate. Tubing shall be suitably sized TP 316L stainless steel with stainless steel double ferrule compression fittings.
11. Solenoid valve shall be selected in accordance with low power type.
12. All on/off valves shall be preferably fitted with single acting, spring return pneumatic actuators, completed with mounting kit.
13. The actuator shall be fail-safe in operation (as specified in data sheets) in loss of electrical signal or loss of air supply.
14. The spring return actuator shall be "pre stressed".
15. Pneumatic actuators will be sized on the basis of a minimum safety factor of 1.25 and a minimum air pressure of 4 Barg. The valve actuator torque shall be in excess of the required valve torque under all operating conditions.
16. All actuators and accessories shall be clearly and permanently identified by nameplate. The nameplate shall be in stainless steel and affixed to the VALVE, actuator and accessories.
17. Partial Stroking test or pilot valve to be considered for 15% of valve closing stroke.
18. Disc/seat material shall be resilient to give a tight shut off feature.
19. Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Temperature:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: -5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % DB FOR Winter HVAC Design: 6 °C
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
20. In services where the differential pressure over the valve results in a temperature drop which Will cause freezing of the stuffing box and ice formation on the stem, extended bonnet shall be provided.Valve stem extension shall be detachable for easy replacements.
21. - At least two stem seals shall be provided with facility for injection of secondary sealant and with stainless steel fittings. - Stem seal shall be replaceable while the valve is in closed operation position.
22. Valves in safety related services should have been fire tested and certification to be provided.
23. Flow direction shall be permanently and clearly indicated on the valve body.
24. External grounding shall be provided for each solenoid valve
25.Short stroke single acting pneumatic piston actuators shall preferably be used on emergency shutdown service.

## ESDV-1701A
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 10
9038 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0005 | D02
On-Off Valve
TAG NO: |  | ESDV-1701A | P&ID NO : |  | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | [6 empty] | SERVICE: |  | FROM W018S
FLUID STATE: | CRUDE OIL |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | 11347.0341 | 10288.03 | 3084.18 | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 94
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 36.31 |  | 36.31 | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 473.9/12.97/917.7 |  | 417.0/12.99/872.7 | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.011/18.99 |  | 0.011/11.28 | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | 52.57 |  | 52.62 | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 291.2 |  | 67.7 | -
LINE | 10 | PIPE LINE SIZE | IN |  | 4" |  |  |  |  | ACTUATOR (Note 25 in Previous Page) | 52 | TYPE |  | Single Acting , Spring Return
|  | PIPE LINE SIZE | OUT |  | 4" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | LN15/ PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 4" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Piping Material Specification | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Acc. to Reference 2 & Note15 in Previous Page )
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | API 60K (Note 3 in Below Table) | [5 empty] | 59 | TRAVELING TIME |  | 5 Sec. (Note 4 in Previous Page)
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END |  |  | 4"/ API 3000 | [5 empty] | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 4"/ API 3000 | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | (Note 23 in Previous Page ) | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-1701A /EZSO-01701A
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  | API 75K (Note 3 in Below Table) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT MATERIAL |  |  | PTFE | [5 empty] | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | SEAT TYPE |  |  | Soft Seat | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | STEM / MATERIAL |  |  | forged, 13% chromium steel (Acc. to Reference 7 & Notes 20,21 in Previous Page) | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | LEAKAGE CLASS |  |  | ANSI Class VI |  |  |  |  | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-1701A | ( (Note 24 in Previous Page) |  |  |  |  | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | Will Be Finilized Later
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes ( Note 22 in Previous Page)
| 49 | VOLUME TANK |  |  | No | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
| (1) PMS: Piping Material Specification |  |  | (2) All material shall be suitable for minimum design metal temperature.
(3) As per Piping Material Specification , Doc No. "BK-SSGRL-PEDCO-110-PI-SP-0001"
(4) Manual Reset to be considered for all Emergency Shut off solenoids as per P&ID.
D02
D02
D02
D02
D02

## ESDV-1701B
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 10
9038 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0005 | D02
On-Off Valve
TAG NO: |  | ESDV-1701B | P&ID NO : |  | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | [6 empty] | SERVICE: |  | FROM W046S
FLUID STATE: | CRUDE OIL |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | 17421.9094 | 7959.52 | 6581.02 | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 94
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 31.6 |  | 15.2 | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 297.1/13.65/970.4 |  | 188.6/13.69/844.3 | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.011/29.67 |  | 0.01/8.314 | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | 96.59 |  | 69.67 | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 1140 |  | - | -
LINE | 10 | PIPE LINE SIZE | IN |  | 4" |  |  |  |  | ACTUATOR (Note 25 in Previous Page) | 52 | TYPE |  | Single Acting , Spring Return
|  | PIPE LINE SIZE | OUT |  | 4" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | LN15/ PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 4" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Piping Material Specification | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Acc. to Reference 2 & Note15 in Previous Page )
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | API 60K (Note 3 in Below Table) | [5 empty] | 59 | TRAVELING TIME |  | 5 Sec. (Note 4 in Previous Page)
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END |  |  | 4"/ API 3000 | [5 empty] | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 4"/ API 3000 | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | (Note 23 in Previous Page ) | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-1701B /EZSO-01701B
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  | API 75K (Note 3 in Below Table) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT MATERIAL |  |  | PTFE | [5 empty] | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | SEAT TYPE |  |  | Soft Seat | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | STEM / MATERIAL |  |  | forged, 13% chromium steel (Acc. to Reference 7 & Notes 20,21 in Previous Page) | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | LEAKAGE CLASS |  |  | ANSI Class VI |  |  |  |  | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-1701B | ( (Note 24 in Previous Page) |  |  |  |  | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | Will Be Finilized Later
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes ( Note 22 in Previous Page)
| 49 | VOLUME TANK |  |  | No | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
| (1) PMS: Piping Material Specification |  |  | (2) All material shall be suitable for minimum design metal temperature.
(3) As per Piping Material Specification , Doc No. "BK-SSGRL-PEDCO-110-PI-SP-0001"
(4) Manual Reset to be considered for all Emergency Shut off solenoids as per P&ID.
D02
D02
D02
D02
D02
D02
D02
D02
D02

## ESDV-1701C
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 10
9038 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0005 | D02
On-Off Valve
TAG NO: |  | ESDV-1701C | P&ID NO : |  | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | [6 empty] | SERVICE: | FROM W008N
FLUID STATE: | CRUDE OIL |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | 11347.0341 | 10288.03 | 3084.18 | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 94
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 46.19 |  | 46.19 | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 443.9/13.05/909.7 |  | 388.9/13.07/864.9 | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.011/15.20 |  | 0.011/9.026 | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | 52.57 |  | 52.62 | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 291.2 |  | 67.7 | -
LINE | 10 | PIPE LINE SIZE | IN |  | 4" |  |  |  |  | ACTUATOR (Note 25 in Previous Page) | 52 | TYPE |  | Single Acting , Spring Return
|  | PIPE LINE SIZE | OUT |  | 4" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | LN15/ PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 4" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Piping Material Specification | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Acc. to Reference 2 & Note15 in Previous Page )
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | API 60K (Note 3 in Below Table) | [5 empty] | 59 | TRAVELING TIME |  | 5 Sec. (Note 4 in Previous Page)
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END |  |  | 4"/ API 3000 | [5 empty] | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 4"/ API 3000 | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | (Note 23 in Previous Page ) | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-1701C /EZSO-01701C
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  | API 75K (Note 3 in Below Table) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT MATERIAL |  |  | PTFE | [5 empty] | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | SEAT TYPE |  |  | Soft Seat | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | STEM / MATERIAL |  |  | forged, 13% chromium steel (Acc. to Reference 7 & Notes 20,21 in Previous Page) | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | LEAKAGE CLASS |  |  | ANSI Class VI |  |  |  |  | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-1701C | ( (Note 24 in Previous Page) |  |  |  |  | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | Will Be Finilized Later
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes ( Note 22 in Previous Page)
| 49 | VOLUME TANK |  |  | No | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
| (1) PMS: Piping Material Specification |  |  | (2) All material shall be suitable for minimum design metal temperature.
(3) As per Piping Material Specification , Doc No. "BK-SSGRL-PEDCO-110-PI-SP-0001"
(4) Manual Reset to be considered for all Emergency Shut off solenoids as per P&ID.
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02

## ESDV-1701D
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 10
9038 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0005 | D02
On-Off Valve
TAG NO: |  | ESDV-1701D | P&ID NO : |  | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | [6 empty] | SERVICE: | FROM W028
FLUID STATE: | CRUDE OIL |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | 29036.5156 | 11939.29 | 9871.53 | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 94
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 44.41 |  | 44.41 | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 266.8/13.60/959.1 |  | 167.7/13.63/833.9 | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.01/23.64 |  | 0.01/6.57 | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | 96.59 |  | 96.67 | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 1140 |  | - | -
LINE | 10 | PIPE LINE SIZE | IN |  | 4" |  |  |  |  | ACTUATOR (Note 25 in Previous Page) | 52 | TYPE |  | Single Acting , Spring Return
|  | PIPE LINE SIZE | OUT |  | 4" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | LN15/ PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 4" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Piping Material Specification | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Acc. to Reference 2 & Note15 in Previous Page )
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | API 60K (Note 3 in Below Table) | [5 empty] | 59 | TRAVELING TIME |  | 5 Sec. (Note 4 in Previous Page)
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END |  |  | 4"/ API 3000 | [5 empty] | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 4"/ API 3000 | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | (Note 23 in Previous Page ) | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-1701D /EZSO-01701D
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  | API 75K (Note 3 in Below Table) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT MATERIAL |  |  | PTFE | [5 empty] | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | SEAT TYPE |  |  | Soft Seat | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | STEM / MATERIAL |  |  | forged, 13% chromium steel (Acc. to Reference 7 & Notes 20,21 in Previous Page) | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | LEAKAGE CLASS |  |  | ANSI Class VI |  |  |  |  | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-1701D | ( (Note 24 in Previous Page) |  |  |  |  | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | Will Be Finilized Later
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes ( Note 22 in Previous Page)
| 49 | VOLUME TANK |  |  | No | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
| (1) PMS: Piping Material Specification |  |  | (2) All material shall be suitable for minimum design metal temperature.
(3) As per Piping Material Specification , Doc No. "BK-SSGRL-PEDCO-110-PI-SP-0001"
(4) Manual Reset to be considered for all Emergency Shut off solenoids as per P&ID.
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02

## ESDV-1701E
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 10
9038 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0005 | D02
On-Off Valve
TAG NO: |  | ESDV-1701E | P&ID NO : |  | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | [6 empty] | SERVICE: | FROM W035
FLUID STATE: | CRUDE OIL |  | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | 29036.5156 | 11939.29 | 9871.53 | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 94
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 40.71 |  | 40.71 | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 274.9/13.60/962.3 |  | 173.3/13.64/836.8 | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.01/25.33 |  | 0.01/7.063 | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | 96.59 |  | 96.67 | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 1140 |  | - | -
LINE | 10 | PIPE LINE SIZE | IN |  | 4" |  |  |  |  | ACTUATOR (Note 25 in Previous Page) | 52 | TYPE |  | Single Acting , Spring Return
|  | PIPE LINE SIZE | OUT |  | 4" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | LN15/ PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 4" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Piping Material Specification | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Acc. to Reference 2 & Note15 in Previous Page )
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | API 60K (Note 3 in Below Table) | [5 empty] | 59 | TRAVELING TIME |  | 5 Sec. (Note 4 in Previous Page)
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END |  |  | 4"/ API 3000 | [5 empty] | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 4"/ API 3000 | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | (Note 23 in Previous Page ) | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-1701E /EZSO-01701E
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  | API 75K (Note 3 in Below Table) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT MATERIAL |  |  | PTFE | [5 empty] | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | SEAT TYPE |  |  | Soft Seat | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | STEM / MATERIAL |  |  | forged, 13% chromium steel (Acc. to Reference 7 & Notes 20,21 in Previous Page) | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | LEAKAGE CLASS |  |  | ANSI Class VI |  |  |  |  | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-1701E | ( (Note 24 in Previous Page) |  |  |  |  | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | Will Be Finilized Later
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes ( Note 22 in Previous Page)
| 49 | VOLUME TANK |  |  | No | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
| (1) PMS: Piping Material Specification |  |  | (2) All material shall be suitable for minimum design metal temperature.
(3) As per Piping Material Specification , Doc No. "BK-SSGRL-PEDCO-110-PI-SP-0001"
(4) Manual Reset to be considered for all Emergency Shut off solenoids as per P&ID.
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02

## ESDV-1701F
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR ON OFF / SHUTDOWN VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 10
9038 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0005 | D02
On-Off Valve
TAG NO: |  | ESDV-1701F | P&ID NO : |  | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | [6 empty] | SERVICE: | FROM W007S
FLUID STATE: |  | CRUDE OIL | PHASE: |  | LIQUID | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | 11614.6062 | 3979.76 | 3290.51 | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 12.78 |  | 12.78 | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 94
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 41.77 |  | 41.77 | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 283.9/13.62/965.7 |  | 186.9/13.68/843.5 | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.012/27.04 |  | 0.01/8.17 | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | 96.59 |  | 96.67 | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 1140 |  | - | -
LINE | 10 | PIPE LINE SIZE | IN |  | 4" |  |  |  |  | ACTUATOR (Note 25 in Previous Page) | 52 | TYPE |  | Single Acting , Spring Return
|  | PIPE LINE SIZE | OUT |  | 4" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | LN15/ PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 4" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Piping Material Specification | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Acc. to Reference 2 & Note15 in Previous Page )
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | API 60K (Note 3 in Below Table) | [5 empty] | 59 | TRAVELING TIME |  | 5 Sec. (Note 4 in Previous Page)
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END |  |  | 4"/ API 3000 | [5 empty] | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 4"/ API 3000 | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | (Note 23 in Previous Page ) | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-1701F /EZSO-01701F
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL / DISK MATERIAL |  |  | API 75K (Note 3 in Below Table) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | SEAT MATERIAL |  |  | PTFE | [5 empty] | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | SEAT TYPE |  |  | Soft Seat | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | STEM / MATERIAL |  |  | forged, 13% chromium steel (Acc. to Reference 7 & Notes 20,21 in Previous Page) | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | LEAKAGE CLASS |  |  | ANSI Class VI |  |  |  |  | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-1701F | ( (Note 24 in Previous Page) |  |  |  |  | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | Will Be Finilized Later
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes ( Note 22 in Previous Page)
| 49 | VOLUME TANK |  |  | No | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
| (1) PMS: Piping Material Specification |  |  | (2) All material shall be suitable for minimum design metal temperature.
(3) As per Piping Material Specification , Doc No. "BK-SSGRL-PEDCO-110-PI-SP-0001"
(4) Manual Reset to be considered for all Emergency Shut off solenoids as per P&ID.
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02
D02