## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1026 |  |  | Transmital Date: 31-May-2022
Document Title: Data Sheets For Diesel Generator |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1026 |  |  | Transmital Date: 31-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بند 2.5 به استاندارد IPS-M-PM-290 (2) اشاره شود. |  | 1401-2294-111571 | 1401-03-31 | اعمال گردید.
2 | بند 3.20 تعداد باتریهای هر بانک با توجه به ولتاژ نامی هر باتری 1.2 برابر با 20 عدد می باشد. |  | 1401-2294-111571 | 1401-03-31 | اعمال گردید.
3 | جهت سایز باتری عبارت بزگتر از 200AH قید گردد. |  | 1401-2294-111571 | 1401-03-31 | مطابق با استاندارد IPS-M-PM-290 بند 6.11.3.1، ظرفیت باتری بیش از 200 آمپرساعت در نظر گرفته شده است.
4 | بند 11.2 ویرایش سوم استاندارد IPS-E-EL-143 لحاظ گردد. |  | 1401-2294-111571 | 1401-03-31 | اصلاح گردید.
5 | بند 11.22 تعداد کابلهای قدرت متصل به تابلو محلی بر اساس مدرک جدول کابل تأیید شده لحاظ گردد. نمایش کابل تک رشته به صورت 1X240 نمایش داده شده است. تعداد کابلها در هر فاز و تعداد کابلهای نول مشخص گردد. |  | 1401-2294-111571 | 1401-03-31 | اصلاح گردید.
6 | با توجه به نهایی نشدن لیست بارها در خصوص بارهای اضطراری و نرمال مقتضی است پس از تأیید بارهای اضطراری توسط این امور، نسبت به تعیین ظرفیت دیزل و ثبت مقادیر در داده برگ اقدام گردد. |  | 1401-2294-111571 | 1401-03-31 | با توجه به به روزرسانی مدرک محاسباتی دیزل ژنراتور، این مدرک مورد بازنگری قرار گرفت. در صورت هرگونه تغییر در لیست بارها، این مدرک ویرایش خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-Jun-2022 |  |  |  |  | Date: