## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0007-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0255 |  |  | Transmital Date: 16-Nov-2021
Document Title: Calculation Note For Diesel Generator Sizing |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0008-EL-TR-0255 |  |  | Transmital Date: 16-Nov-2021
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-CN-0007-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised base on comments on load list and shall be submitted as IFA after finalizing or minor comments on load list. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | در صورت وجود هر گونه تغییر احتمالی در ایست بار، این مدرک به روزرسانی خواهد شد.
2 | Emergency loads table shall be added to this document as separated sheet base on load list. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | لیست بارها بر روی باسبار اضطراری اضافه گردیده است.
3 | Total power of AC&DC UPS In the emergency loads table shall be considered for diesel sizing. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | مطابق با لیست بار، بارهای بر روی UPS و DC Charger به صورت Continuous بر روی دیزل ژنراتور قرار داده شده است.
4 | It shall be clarify where the biggest motor starting power has been considered in diesel sizing on page 7, section 4.2. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است.
5 | It shall be clarify why temperature derating factor has been considered again in diesel sizing on page 7, section 4.4. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است.
6 | Editing error shall be modified on page 8, section 5.1. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است.
7 | As per equipment list prepared in basic design, considered ambient temperature shall be 55 degree centigrade. Therefore all mentioned 48 degrees in this document shall be modified to 55. also considered derating factor shall be related to 55 degree centigrade. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است.
8 | The calculated Load kVA during starting of biggest motor (on page 8, section 5.2) shall be calculated base on total apparent power. (219.8KVA is not total apparent power) |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است.
9 | The value of voltage dip base on appendix 3 shall be specified on page 9, section 5.3. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است.
10 | The used formula for calculating of apparent power for Motor Starting and Total sum of kVA delivered by generator to start shall be explained in detail on page 8, section 5.2. |  | BK-SUR-ENG-ELE-00-02130 | 2021-11-28 | محاسبات بر اساس آخرین لیست بار به روزرسانی گردیده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 28-Nov-21 |  |  |  |  | Date: