## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1026 |  |  | Transmital Date: 31-May-2022
Document Title: Data Sheets For Diesel Generator |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1026 |  |  | Transmital Date: 31-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Next revision shall be issued after finalizing or minor comments on load list, Diesel generator sizing and LV switchgear single line diagram. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | با توجه به به روزرسانی مدرک محاسباتی دیزل ژنراتور، این مدرک مورد بازنگری قرار گرفت. در صورت هرگونه تغییر در لیست بارها، این مدرک ویرایش خواهد شد.
2 | General, Item 2.4: IPS-M-PM-290 (1), Material and Equipment Standard for Reciprocating Internal Combustion Engines and IPS-E-EL-100(1) shall be added as reference document. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | اعمال گردید.
3 | Generator Specification, Item 14.1: As per IPS-M-EL-138 (1) part 6.4, noise level at 1m should not normally exceed 81 dB (A) in the no load running condition. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | اضافه گردید.
4 | Generator Specification, Item 10.8: According to Diesel generator specification section 4.5, Permissible overload shall be considered as below: 10% of rated current for a period of one hour (in each 12 hours function) |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | اضافه گردید.
5 | Control Panel, Item 11.13, 11.17: The protection shall be revised after finalizing or minor comments on LV switchgear single line diagram. (For example base on IPS-E-EL-100(1), there is not need to 49T, 51G and 64R) |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | مدرک تک خطی اصلاح گردیده است. در صورت نیاز در ویرایش های بعدی اصلاحات مربوطه لحاظ خواهد شد.
6 | Page 6, Items 10.17&10.18: According to basic electrical design criteria and IPS-M-EL-138(1), Insulation class and temperature rise shall be modified to "F", "B" instead of "H" and "F". |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | اعمال گردید.
7 | Switching Device, Item 12.9: Rated short circuit level shall be updated based on short circuit calculations. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | بعد از نهایی شدن مطالعات شبکه این قسمت به روزرسانی خواهد شد.
8 | Control Panel, Item 11.10: Switching Device, Item 12.6: Rated current shall be rechecked and modified after finalizing or minor comments on diesel sizing (If required). |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | اصلاح گردید.
9 | General Specification, Item 10.39: Voltage regulation shall be modified to ±5%. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | اعمال گردید.
10 | General Specification, Item 10.21: Short circuit level shall be specified by consultant base on short circuit calculation, not by vendor. |  | BK-SUR-ENG-ELE-01-04696 | 2022-06-14 | بعد از نهایی شدن مطالعات شبکه این قسمت به روزرسانی خواهد شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 14-Jun-2022 |  |  |  |  | Date: