| Item No. | Clarification Description(Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- |
| - GENERAL |  |  |  |  |  |  |
|  | VENDOR shall confirm his full compliance to meet purchaser’s specifications, code and standard listed in specifications and mechanical data sheets, PIDs, Plot Plans and etc. Any deviations which not mentioned in deviation list will not be accepted by purchaser at detail stage. If there is not any Deviation or Exception from purchaser’s technical documents, VENDOR shall be signed with "NO DEVIATION" and submitted with his proposal. | OK we confirm. | Noted. Closed. |  |  |  |
|  | VENDOR is sole responsible to consider this clarification and modify his offer based on this TCL. All modifications which need to be considered on the next revision of offer based on this clarification should be clearly marked with revision and cloud marks. All consequences due to changes without cloud mark are in VENDOR’s responsibility. Anyway, this clarification has priority over the offer. | OK we confirm. | Noted. Closed. |  |  |  |
|  | The VENDOR shall have overall responsibility for the coordination with his Sub-Vendors, and for the proper execution of any accessory item assembly, testing, delivery and any other service defined herein. | OK we confirm. | Noted. Closed. |  |  |  |
|  | All equipment shall be designed to meet the requirements shown in the Project Specification and data sheets. | OK we confirm. | Noted. Closed. |  |  |  |
|  | All documents required after purchase order shall be submitted in accordance with VENDOR documents requirements of the PMR. | OK we confirm. | Noted. Closed. |  |  |  |
|  | All required special tools shall be considered in VENDOR main offer (they shall be supplied by bidder without any cost impact). A qualified and complete list has to be included in the bid documentation | OK we confirm. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification mentioned in PMR. | OK we confirm. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm project performance and mechanical guarantee based on data in PMR. | OK we confirm. | Noted. Closed. |  |  |  |
|  | VENDOR should confirm that all sub-vendors shall be selected from project Approved Bidder List (A.V.L.). In case of any deviation, bidder shall submit his deviation list for purchaser. Also VENDOR is fully responsible for his Sub-vendors. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Material specification consists of class and relative grade shall be submitted by detail based on ASME/ ASTM for the whole package. VENDOR shall prepare material and material grade as per data sheets of equipment. Any substitution shall be expressed in deviation form. Meanwhile substitution after Purchase order is not approved. | OK we confirm. | Noted. Closed. |  |  |  |
|  | VENDOR to confirm his compliance with documents priority stated in PMR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement. | OK we confirm. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm that surface preparation and painting of all equipment material including valves, pipes, fittings and everything within the package are in accordance with project painting specification. | OK we confirm. | Interconnecting pipe & valves (between bundles & bays) to be supply by vendor. | OK we confirm. | Noted. Closed. |  |
|  | PURCHASER’s approval shall in no way be construed as relieving VENDOR of any of his obligation, responsibilities or liabilities under the CONTRACT and/or applicable Codes and Standards. | OK we confirm. | Noted. Closed. |  |  |  |
|  | In case of order, PURCHASER would not review documents sent by VENDOR before receiving VENDOR Print Index and Schedule. VENDOR Print Index and Schedule (VPIS) shall be prepared as first document after PO. All documents shall be issued after getting approval of this mentioned document. | OK we confirm. | Noted. Closed. |  |  |  |
|  | In case of order, VENDOR should provide her quality control plan (VQCP) based on requirements specified on MR and its attachments and also VENDOR’s experiences and send for approval. PURCHASER’s ITP and relevant specifications attached to MR are minimum requirement and VENDOR should consider them as a base and provide comprehensive Quality Control Plan. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Providing Required Facilities for Inspection and Test shall be in VENDOR’s Scope of work. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Utility consumption summary shall be submitted by VENDOR along with his proposal. | OK we confirm. | Noted. Closed. |  |  |  |
|  | All static and dynamic loads on foundations/Steel Structures shall be specified by VENDOR. | OK we confirm After PO | Noted. Closed. |  |  |  |
|  | All Native files of drawings & calculations (like CodeCalc; FEA; ANSYS; HTRI file; Auto-CAD DWG,..) shall be provided by bidder at detail stage. | OK we confirm. | Noted. Closed. |  |  |  |
|  | S.S. Name plates shall be fitted to all machines and equipment, according to project standard DWG. | OK we confirm. | Noted. Closed. |  |  |  |
|  | VENDOR shall submit the documents which are specified at “BID stage”. Fail to submit the necessary documents will be deemed as offer is disqualified. | OK we confirm. Any information that will be specified after detail design cannot be submitted in bid stage. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm that project PMS will be followed for all pipes, valves, gaskets, etc. and also for Tie-in points in battery limit. | OK we confirm. | All the inter-connecting pipes and valves, as well as flanges and fittings, and in general all the inter-connecting components to be supplied by vendor, please confirm. | OK we confirm. | Noted. Closed. |  |
|  | VENDOR shall consider all required consumable materials for site welding, inspection, tests and etc. of equipment, piping, structures and.... | OK we confirm. | Noted. Closed. |  |  |  |
|  | No fabrication shall be commenced until complete calculations. Shop drawings have been received and approved by purchaser. | OK we confirm. | Noted. Closed. |  |  |  |
|  | External supports & attachments, clips for piping (wherever required) shall be supplied by VENDOR. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Please confirm that all spare parts (commissioning and two years) shall be sent with the equipment to site at the same time. | OK we confirm. | The spare parts should be packed and marked properly before the shipment at vendor’s shop. Packing should be done in accordance with packing and shipping procedure and should be done in a way that the keeping at the ware house will be possible properly. Please confirm. | OK we confirm. | Noted. Closed. |  |
|  | Vendor shall provide in his quotation, recommended spare parts list compatible with job specification for commissioning, two years of normal operation and capital spares with unit price and their validity period. Recommended spare parts shall have full description and enough data in accordance with related job specification (PMR & NIOEC-SP-40-03 & Doc. No. E&D-QC-SP-1). | OK we confirm. | Noted. Closed. |  |  |  |
|  | Please confirm, any loose items include of electrical & instrument local panel, cables and pipes on battery limit of each equipment will be supplied by vendor. | OK we confirm. | Inter-connecting piping (If applicable) is in vendor’s scope of work and supply. Please confirm. | OK we confirm. | Noted. Closed. |  |
|  | For all pressure parts and those required special consideration (such compliance with NACE) as well as for supports the material certificate should be in accordance with EN 10204, 3.1. Material certificate for non-pressure parts shall be in accordance with EN 10204, 2.2. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Please confirm that all the attached documents listed in attachment No.1 of the material requisition with Ref. BK-GCS-PEDCO-120-ME-MR-0004_D00 are already in your possession. Some updated documents (latest revision) were handed over with this TCL. | OK we confirm. | Noted. Closed. |  |  |  |
| - PROCESS |  |  |  |  |  |  |
|  | Fan diameter shall be input in your thermal file. | OK we confirm. | Noted. |  |  |  |
|  | Nozzle sch. Shall be considered based on preliminary mechanical design and have good margin for real mechanical design. | OK we confirm. | Nozzle material is S.S 316 L, so selected nozzle data base in your file shall be edited and revised. | OK we confirm. | Noted. Closed. |  |
|  | Total tube sheet thickness plus tubes extend from tube sheets as mechanical consideration shall be input in KMC thermal file. | OK we confirm. | Noted. |  |  |  |
|  | Un finned tube length shall be inserted in the thermal file. | OK we confirm. | Noted. |  |  |  |
|  | Thermal design shall be based on min. humidity and fan selection shall be based on Max. humidity. | OK we confirm. | Min ambient temperature should be modified in thermal files. | OK we confirm. | Noted. Closed. |  |
|  | With considering exchanger location on the ground, ground clearance to the bundle and plenum height shall be input in KMC thermal file. | OK we confirm. | Noted. |  |  |  |
|  | Fin density selected in thermal file AE-2101 is not correct. | OK we confirm. | It’s 400 fin/meter.FPI is 10.2?? please edit it | OK we confirm. | Noted. Closed. |  |
|  | Please Consider design barometric pressure0.9142 bar. | OK we confirm. | Noted. |  |  |  |
|  | Please consider minor changes in heat curve for your new design. | OK we confirm. | Noted. |  |  |  |
|  | Please add and consider all PDS notes in your design too. | OK we confirm. | Fluid flow rate and temperature shall be modified based on latest PDS. | OK we confirm. |  |  |
|  | Total drop for fan selection shall be total static pressure drop plus 20percent of drop of air across the bundle. | OK we confirm. | Noted. |  |  |  |
|  | New comments: - Max ambient temperature shall be input. - Fan shaft lane width & number shall be input in thermal files. - Fin geometry type (extruded) shall be specified in thermal files. - Design case shall be run in rating mode and the other case shall be run in simulation mode and reported in your data sheet. - Please do not specify duty in your thermal file (AE-2102). - Tube wall thk. is 2.11 mm which is higher than STD based on tube material (S.S 316 L). Please recheck and modify. - Please recheck tube pitch selected. | - OK we confirm. - Since motor of fans are considered to be located above (near the fans), there’s no need to specify this part. - OK we confirm. - OK we confirm. - OK we confirm. - OK we confirm. - Tube pitches are considered correctly and they’re considered little more to reduce static pressures in thermal design. |  |  |  |  |
|  | New item: Please remove the difference between inlet temperature in Hirgan’s data sheet and technical proposal in case 2102-summer case. |  |  |  |  |  |
|  | New item: Please revise the minimum ambient temperature in case 2102-winter case. |  |  |  |  |  |
| - MECHANIC |  |  |  |  |  |  |
|  | Following documents shall be submitted; 1.Sub-vendor list 2.Deviation list (project deviation format shall be signed and attached) 3.Quality plan 4.All revised general arrangements based on new thermal design 5.Air cooler estimated weight 6.Delivery plan 7.Reference list | OK we confirm. | Noted. Closed. |  |  |  |
|  | Breakdown price of following items shall be included in the proposal, as well as total price. 1) Material and Fabrication for each Section Separately 2) Pre-commissioning & commissioning spare parts (END-QC-SP-1) 3) 2 years operational spare parts (END-QC-SP-1) 4) Packing & transportation 5) Other fee (if any) | OK we confirm. | Noted. Closed. |  |  |  |
|  | Vendor to confirm the project specifications with Ref. BK-GCS-PEDCO-120-ME-SP-0001_D00 and BK-GNRAL-PEDCO-000-ME-SP-0001_D00 are also considered for design of air coolers in addition of ASME Sec. VIII Div.1 and API 661. Also IPS standards IPS-E-PR-785 and IPS-G-ME-245 are to be considered. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Following works to be considered as exclusion of vendor scope; 1.Fire proofing material 2.Permanent gasket and bolt of process nozzle | OK we confirm. | Inter connecting bolt and nuts, as well as gaskets and pipes (If required) to be supplied by vendor. Please confirm. | OK we confirm. |  |  |
|  | Following items shall be quoted as option in vendor proposal: 1- Shop & site run in test (including vibration verification) Noted that trial assembly to be included in shop run in test (for one bay per item). 2- Site supervision for installation Please confirm and revise your offer. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Mechanical guarantee and Guarantee period to be included in BID. | OK we confirm. | Noted. Closed. |  |  |  |
|  | A summary table of air coolers including items No, unit No, Bay No., bundle No., weights and power consumption is needed in vendor proposal. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Vendor should consider all Mechanical data sheet notes and implement them on their designs and data sheets. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Bidder shall confirm to verify nozzle external loads calculations according to API 661 PART 7.1.10 by Finite Element Analysis (nozzle loads shall be used two (3) times of API 661). Please add it as a note in relevant data sheets. | There is discrepancy in this item. ( nozzle loads shall be used two (3) times of API 661) | 3 X API nozzles loads to be taken into consideration, please confirm. | OK we confirm. |  |  |
|  | Vendor shall consider bundle expansion on structure. | OK we confirm. | Consequently, sliding pad on the sliding header to be provided by vendor, its material and characteristics to be the same as project specifications / reference standards, sliding header to be considered oppose to the front header (Where the nozzles located), please confirm. | OK we confirm. |  |  |
|  | Possibility of lateral header movement to be considered by vendor. | OK we confirm. | Mechanical calculations for lateral force to be also done. | OK we confirm after PO. |  |  |
|  | Requirements of Expanded tube to tube sheet joint, No. of grooves should be followed as per clauses 9.3.2, 9.3.3 of API 661 and TEMA Class R requirements. As regards special services like H2S, lethal and hydrogen services strength welding is required. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Tube hole diameters, tolerances, grooving and finish shall be in accordance with TEMA Class R. Tubes shall be expanded into the tube sheet up to within 3mm (1/8") of the airside face of the tube sheet. Minimum tube sheet thickness shall be 25 mm. | OK we confirm | In no case the expansion length shall not be less than the tube O.D. please confirm. | OK we confirm. |  |  |
|  | The minimum thickness of tube sheets and plug sheets in case of plug type headers and removable cover plate headers shall be in accordance with TEMA standard but shall not be less than 25mm including corrosion allowance. | OK we confirm. Minimum thickness will be according to API 661 for each type of material. | Please confirm that TEMA standard will be followed along with API 661. | OK we confirm. |  |  |
|  | On the side frames there shall be lugs for lifting the bundles stiffly welded to the side members and with a hole of 25 mm minimum. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Fan guards for air coolers shall be furnished to provide personnel protection during operation. | OK we confirm. | Air seal to be provided on bundle in order not to let the air flows from the hollow spaces. | OK we confirm. |  |  |
|  | No carbon steel parts to be welded shall have a carbon content higher than 0.25%. please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Material requirement should be in compliance with NACE MR 0175/ISO 15156 and Technical Specification for Material Requirements in Sour Service Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0008. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Corrosion allowance shall be multiplied by two for pass partition plates or stiffeners. Please confirm. | Not applicable for S.S. material. | Noted. Closed. |  |  |  |
|  | All header flanges shall be welding neck type. Vent and drain nozzle shall be 2” LWN type with ASME rating flange and blinded. All nozzles smaller than 2” to be LWN. Please confirm and revise your technical offer accordingly. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Hydrostatic test shall be in accordance with the requirements of ASME code Sec. VIII Div.1. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | All butt welds in headers shall be examined by full RT. All corners welds shall be full UT. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Fan rings, Fan deck, Plenum, walkway grating including boltings shall be hot dip galvanized | OK we confirm. | Noted. Closed. |  |  |  |
|  | Material of louver blades (if required) shall be high quality galvanized carbon steel. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | TI/PI and vent and drain nozzle sizes shall be specified in relevant data sheet. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Fan performance curves for all fans shall be included to relevant data sheet in quotation. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Bidder to clarify mechanical efficiency of separate power transmissions Em value and related reference. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Access Platform, Maintenance Platform (if required) and Ladders for access to platforms and platform’s gratings are in vendor scope of supply. please confirm Access Platform: Shall be provided on all the four sides. Maintenance Platform : Full steel platform duly interconnected along full length and width of air coolers for fan/motors etc. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Platforms shall be a minimum of 750 mm wide and 2 m headroom. Design load of platforms shall be 500 kg/m^2. | OK we confirm. | Noted. Closed. |  |  |  |
|  | The effect of the pipe supports loads on your structure shall be borne by your side without cost impact according to your experience. just the additional price for pipe support steel structure weight can be paid. | The specified weight of the structure is according to KMC experience, however the price will be submitted per kilogram. | Noted. Closed. |  |  |  |
|  | For gasket material and relevant flange specification of blinded flanges, vendor shall follow Piping material specification. | OK we confirm. | Gaskets for nozzles shall be spiral wound type, graphite filled with inner ring S.S.316 and outer ring S.S 316. Please confirm. | OK we confirm. |  |  |
|  | A vibration switch shall be provided one per motor for each bay within the equipment. The mounting location shall be carefully selected to represent high vibration / trip in case of bearing / fan damage and ease of maintenance. | OK we confirm | Vibration switch type and locations to be clearly shown on the GA. Drawing. Please confirm. | OK we confirm after P.O. |  |  |
|  | Motors electrical area classification and service factor shall be specified. | OK we confirm. | Temperature classes T3, shall be specified in revised offer by vendor. | OK we confirm. |  |  |
|  | Minimum stock thickness for extruded fins shall be 0.40 mm. This thickness shall apply at the root of the fin. Fins Stock thickness shall be specified in related data sheet. | The fin thickness is according to KMC finning machine. (thermal calculation will be issued accordingly) | Fin characteristics to be considered same as this clause. Vendor’s offer to be the same also. | OK we confirm. |  |  |
|  | The maximum allowable number of fins is 400 per meter of the tube length. In order to prevent fouling, fin surfaces shall be smooth. | OK we confirm. | Noted. Closed. |  |  |  |
|  | The width of the tube bundle shall be chosen with due regard to transport and handling aspects, and shall not, in general, exceed 3 meters. At least one inlet nozzle is required per meter of bundle width. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Spare part for commission and 2 years are included at scope of supply and not as optional. | OK we confirm. The basis is QTY not Percentage. | Quantity or percentage whichever is greater to be taken into consideration. | OK we confirm. |  |  |
|  | Please confirm to consider the following items in spare parts for pre-commissioning, commissioning and start-up in the scope of supply. Plug: 10% Plug gaskets: 10% (min. 2 sets). Standard bearing: minimum 20% per size and type and material Gaskets for blind nozzles: 100% (min. one set of gasket per each type) Stud bolts & nuts & washer : 5% (min. 2 sets). | OK we confirm. For interchangeable spares, spare parts are considered just for one bundle. | Spare parts to be considered for the whole unit. | OK we confirm. |  |  |
|  | Please confirm to consider the following items in spare parts for 2 years operation in the scope of supply. Plugs Steel 1% & Nonferrous 2% (minimum one number) Plug gasket 5% (minimum one number) Tube support 10% (minimum one number) Gaskets for blind nozzles: 200% (min. two set of gasket per each type) Stud bolts & nuts & washer: 10% (min. 2 sets). The following items as per project requirements attached to MR. Blade Bearings Belts Bolting for Structure Fan Blades Vibration Detectors | OK we confirm. For interchangeable spares, spare parts are considered just for one bundle. | Plugs steel and nonferrous are not mentioned. Minimum quantities are not specified in technical proposal please confirm. Spare parts to be considered for the whole unit. | OK we confirm. |  |  |
|  | Please confirm to consider the following items in Special tools in the scope of supply as minimum. 1-Level Gauge for Pitch Angle Setting of Fan Blades 2-Torque Wrench for Fan Blade Setting Bolts 3-Torque Wrench for Header Plugs | OK we confirm. For interchangeable spares, spare parts are considered just for one bundle. | Spare parts to be considered for the whole unit. | OK we confirm. |  |  |
|  | Preservation (N2 purging) shall be considered in vendor scope of supply / work. Please reconfirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | All plates used in sour service shall be examined by ultrasonic test for lamination, please confirm compliance. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Belt drivers shall be anti-static, Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | All driver, fans, bearings shall be waterproof for outdoor installation. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Earth lugs is in vendor scope of supply. shall be considered, Please revise your offer accordingly. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Rotor shaft power at API point shall be specified at all fan characteristics and fan performance curves. Please revise your offer accordingly. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Structure surface preparation and coating shall be hot deep galvanized (ASTM A123). Please confirm and revise offer accordingly. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Fan hub shall be hot deep galvanized. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Air humidity to be corrected in fan data sheet. Worse case humidity shall be considered in fan calculation.(100%) | OK we confirm. | Noted. Closed. |  |  |  |
|  | Half of fans (50%) shall be equipped with variable pitch automatic system to control fluid temperature, please revise offer accordingly. Related data sheet for fan. This price shall be included SS 316 Tube fitting, actuators, positioner, IP convertor and all necessary parts for pneumatic circuit. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Draft type of fans is induced, Please revise offer accordingly. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Plug gasket to be solid metal. Please confirm. | OK we confirm. | Noted. Closed. |  |  |  |
|  | The last pass of tubes shall be 1% slope. Please revise your offer accordingly. | OK we confirm. For two phase and liquid phase only. | Noted. Closed. |  |  |  |
|  | Connecting walkway to be considered, please revise technical offer accordingly. | OK we confirm. | Noted. Closed. |  |  |  |
|  | Design pressure and temperature for 2nd Stage Gas Air Coolers to be revised as per PDS. | OK we confirm. | Noted. Closed. |  |  |  |
|  | New item: Fluid rate is dissimilar to Hirgan's data sheet. Please remove the discrepancy. | OK we confirm. |  |  |  |  |
|  | New item: Inlet temperature in both summer and winter case is different with Hirgan's data sheet. Please remove the discrepancy. | OK we confirm. |  |  |  |  |
|  | New item: minimum ambient temperature is incorrect according to Hirgan's data sheet. please revise HTRI file and Technical proposal. Ambient temperature effects on motor power fan please revise thermal design. | OK we confirm. |  |  |  |  |
|  | New item: face velocity is better to consider between 3 and 5. please revise. | OK we confirm. |  |  |  |  |
|  | New item: nozzle schedules should be finalized after mechanical design. | OK we confirm. |  |  |  |  |
|  | New item: Tube layout should be in technical proposal. | OK we confirm. |  |  |  |  |
|  | New Item: Attached, you may find the TBA form which is brought to you for filling out. | OK we confirm. |  |  |  |  |
| - PIPING & MATERIAL |  |  |  |  |  |  |
|  | G.A Drawing (Detail Drawing) of Equipment shall be submitted by vendor after PO. | OK we confirm. | Closed. |  |  |  |
|  | In Vendor Technical Offer in page 16-17 of 66, for AE-2101 rating of nozzles shall be 300#. | OK we confirm. | Closed. |  |  |  |
|  | In Vendor Technical Offer in page 26-27 of 66, for AE-2102 rating of nozzles shall be 600#. | OK we confirm. | Closed. |  |  |  |
|  | In Vendor Drawing, both Inlet & Outlet nozzles shall be in one end of Air Cooler. | OK we confirm. | Closed. |  |  |  |
|  | In Vendor Drawing, Elevation of TOS (Top of Structure) will be at least 5.5 meter. | OK we confirm. | Closed. |  |  |  |
|  | VENDOR shall specify maximum allowable forces and moments at the nozzles for review and purchaser approval. In case of unavoidable over loaded at the nozzles, then the loads should be submitted to the VENDOR for consideration and approval. | OK we confirm. | Closed. |  |  |  |
|  | Surface preparation & coating shall be acc. to "Specification for Painting" with Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006. | OK we confirm. | Closed. |  |  |  |
|  | Radiographic test shall be done (100%). | OK we confirm. RT test cannot be done for corner welds. | Closed. |  |  |  |
|  | Structural steels should be SA-36 (H.D.G). | OK we confirm. | Closed. |  |  |  |
|  | Louver shall be SA-283 Gr. C (H.D.G). | OK we confirm. | Closed. |  |  |  |
|  | All external bolts and nuts shall be hot dip galvanized. | OK we confirm. | Closed. |  |  |  |
|  | Gasket shall be spiral wound type, graphite filled with inner ring S.S.316 and outer ring S.S. 316. | OK we confirm. | Closed. |  |  |  |
|  | Plug material shall be SA-182 F316L. | OK we confirm. | Closed. |  |  |  |
| - INSTRUMENT & CONTROL |  |  |  |  |  |  |
|  | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0004 for package control type.( for this package Type B only Electrical LCP is required). Signals from Vibration switch and signal to I/p Converter shall be transferred to pland ESD/DCS). VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | OK we confirm. BK-GNRAL-PEDCO-000-IN-SP-0004 file hasn’t been sent to us. | Closed. |  |  |  |
|  | Regarding supplying instrument on datasheet), bidder is requested to consider all instruments mentioned on project datasheet. VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0001 for instrumentation devices and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list | OK we confirm. | Specification for switch: •The switches shall be EExd, IIB T4 and the weatherproof requirements of IP-65 as per IEC-60529. •Switch element shall be of the micro switch snap action type and hermetically sealed. Micro-switches shall be two double pole double throw (DPDT) type •The switch contact rating shall be 110VAC @10Amp. •Repeatability shall be ±1% or better of full scale •The accuracy of the pressure switch assembly shall be at least 1% of the span | OK we confirm. |  |  |
|  | - VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0010 for cables and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | OK we confirm. | Closed |  |  |  |
|  | Instrument selection, connection & cabling (including vibration switches, I/P converters and 50% fans controlling devices) shall be acc. to "Specification For Instrumentation" Doc. No. BK-GNRAL-PEDCO-000-IN-SP-0001 | OK we confirm. | Closed |  |  |  |
|  | All terminals shall be screw type. VENDOR shall note that each core/pair/etc. of cable shall be wired to dedicated terminal | OK we confirm. | Closed |  |  |  |
|  | VENDOR shall specify the estimated power required (non-UPS and UPS) | OK we confirm. | Vendor description is required. | OK we confirm. |  |  |
|  | Cable from LCP/Instruments to Control/Electrical building is by contractor except for special cables( if it is not as per our specifications) which shall be supplied by vendor. | OK we confirm. | Closed |  |  |  |
|  | 50% of fans shall be AV type. All required accessories to be considered. | OK we confirm. | Closed |  |  |  |
|  | Vibration switch to be (EExd,IIB,T4, IP65, suitable for 110V@1A rating with 24VDC signal ), please confirm. | OK we confirm. | 110V@10A rating is correct. | Please clarify if there’s reset coil or not. If yes, this 100V is related to reset coil or contact rate or both? Please clarify voltage level in this condition. | Both. |  |
| - SAFETY |  |  |  |  |  |  |
|  | All electrical equipment shall be certified for Zone IIB, T3. | OK we confirm. | Closed. |  |  |  |
|  | The sound pressure level anywhere in the work area shall not exceed 85 dBA. | OK we confirm. | Closed. |  |  |  |
| - ELECTRICAL |  |  |  |  |  |  |
|  | Electrical system scope of work shall be clarified by vendor & any deviation shall be reported. | OK we confirm. | Closed. |  |  |  |
|  | Vendor list & sub vendor list of manufacture shall be according to project AVL. | OK we confirm. | Closed. |  |  |  |
|  | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. (IPS-E-EL-100) | OK we confirm. | Closed. |  |  |  |
|  | Motor shall be manufactured & tested in accordance with the latest applicable sections of the IEC standards. Project specification shall be applied as well. | OK we confirm. | Closed. |  |  |  |
|  | Environmental criteria for design of electrical systems that shall be considered by vendor (According to Electrical System Design Criteria) | OK we confirm. | Closed. |  |  |  |
|  | Hazard Area classification, Gas group and temperature class of motor shall be at least Exd, IIB, T3, with protection degree of IP54 for motor enclosure and IP55 for terminal box. | OK we confirm. | Closed. |  |  |  |
|  | All accessories related to cable entry/termination in electrical equipment (motors, JBs, etc.) such as cable glands & etc. shall be supplied by vendor. | OK we confirm. | Closed. |  |  |  |
|  | Load list shall include all motor & non-motor (if there is). For motors, Mechanical power (BHP), Rated power, efficiency, power factor and rated current shall be specified in the proposal. | OK we confirm. Will be submitted after PO. | Closed. |  |  |  |
|  | API factor, effect of ambient condition especially de-rate factor for altitude shall be considered for specifying rated power of motor and procedure of obtaining rated power of motor from BHP shall be cleared in the proposal. | OK we confirm. | Closed. |  |  |  |
|  | A complete set of spare parts for commissioning shall be supplied for each motor. | OK we confirm. | Closed. |  |  |  |
|  | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | OK we confirm. | Closed. |  |  |  |
|  | Supplier shall design the routing of the power & control cable inside package. | OK we confirm. | Closed. |  |  |  |
|  | Supply of cables between Junction boxes and Package control panel is in vendor scope of work. In other word, All cabling listed in “Customer cable table” shall be supplied and connected by customer/contractor. Cables shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0014”. | OK we confirm. | Closed. |  |  |  |
|  | If UPS & batteries are required, vendor shall provide all necessary documents (such as calculation, list etc.) & supply required equipment according to purchaser standards. | OK we confirm. | Closed. |  |  |  |
|  | According to Project Electrical Load List, there are 12 number of Air cooler Fans. Vendor load list shall be Issued. Project Load List has been attached to document file. | OK we confirm. | Closed. |  |  |  |
|  | LCS in not in vendor scope of work. Client will supply LCSs for start & stop of electrical motors. |  |  |  |  |  |
| - CIVIL & STRUCTURE |  |  |  |  |  |  |
|  | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2. also according to ASCE 7 (2010) Seismic Zone is equal to Zone 3 with Seismic Importance Factor 1.25 . Besides according to INBC-Part 6 amount of Wind Speed shall be considered 120 Km/hr. It is necessary to consider the above in the data sheets. | OK we confirm. | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2 with specific gravity 0.3. Besides, based on ASCE 7-2010 soil is considered in class D. Please consider below parameters in your calculations: Ss = 1.25 S1 = 0.58 Site Coefficient Fa =1.0 Site Coefficient Fv =1.5 SMS=Fa SS SM1=FV S1 PGA = 0.3 Site Coefficient FPGA = 1.2 SDS =0.83 SD1 =0.58 | OK we confirm. |  |  |