| Item No. | Clarification Description(Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.01) |  | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.02) |  | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - GENERAL |  |  |  |  |  |  |  |  |
|  | VENDOR shall confirm his full compliance to meet purchaser’s specifications, code and standard listed in specifications and mechanical data sheets, PIDs, Plot Plans and etc. Any deviations which not mentioned in deviation list will not be accepted by purchaser at detail stage. If there is not any Deviation or Exception from purchaser’s technical documents, VENDOR shall be signed with "NO DEVIATION" and submitted with his proposal. | Confirmed/We think that electrical battery limit is not clear in PID. As instrument we have only considered vibration switch, IP Convertor, and LCP. (LCP as option) Please confirm/clarify? We have not considered any junction box or cable in our scope. Please confirm/clarify? Air Cooler design is based on API 661 7TH EDISTION+ ASME VIII div 1 + IPS 245 and BK-GCS-PEDCO-120-ME-SP-0001_D00 (specifications for air cooled heat exchangers) | For instrument & Electrical clarification refer to related section | For Damafin Reply, refer to related section. |  |  |  |  |
|  | VENDOR is sole responsible to consider this clarification and modify his offer based on this TCL. All modifications which need to be considered on the next revision of offer based on this clarification should be clearly marked with revision and cloud marks. All consequences due to changes without cloud mark are in VENDOR’s responsibility. Anyway, this clarification has priority over the offer. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | The VENDOR shall have overall responsibility for the coordination with his Sub-Vendors, and for the proper execution of any accessory item assembly, testing, delivery and any other service defined herein. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All equipment shall be designed to meet the requirements shown in the Project Specification and data sheets. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All documents required after purchase order shall be submitted in accordance with VENDOR documents requirements of the PMR. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All required special tools shall be considered in VENDOR main offer (they shall be supplied by bidder without any cost impact). A qualified and complete list has to be included in the bid documentation | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | VENDOR shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification mentioned in PMR. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | VENDOR shall confirm project performance and mechanical guarantee based on data in PMR. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | VENDOR should confirm that all sub-vendors shall be selected from project Approved Bidder List (A.V.L.). In case of any deviation, bidder shall submit his deviation list for purchaser. Also VENDOR is fully responsible for his Sub-vendors. | Please send project AVL. We have also send Damafin AVL in rev.0 but we didn’t receive your feedback. | Our AVL of project is M.O.P. vendor shall follow that. M.O.P with together this TCL will be sent for vendor. | Confirmed. |  |  |  |  |
|  | Material specification consists of class and relative grade shall be submitted by detail based on ASME/ ASTM for the whole package. VENDOR shall prepare material and material grade as per data sheets of equipment. Any substitution shall be expressed in deviation form. Meanwhile substitution after Purchase order is not approved. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | VENDOR to confirm his compliance with documents priority stated in PMR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | VENDOR shall confirm that surface preparation and painting of all equipment material including valves, pipes, fittings and everything within the package are in accordance with project painting specification. | Confirmed. According to PID, battery limit is inlet / out let nozzle of air cooler and there is no piping, valves, fitting in Damafin Scope. Please confirm? | Interconnecting pipe & valves (between bundles & bays) to be supply by vendor. (If Any) | Piping Calculations is not in Damafin scope, if You want any piping be in Damafin scope, please provide isometric plans; Or if you mean vent & drain interconnecting pipings, please clarify? You have 3 different units for each item, each unit has only one bay/bundle; we think there is no interconnecting piping actually, just fluid in one pipe might be distributed between different units. |  | Since it has only one bay/bundle, there is no need to consider interconnecting piping for it. |  |  |
|  | PURCHASER’s approval shall in no way be construed as relieving VENDOR of any of his obligation, responsibilities or liabilities under the CONTRACT and/or applicable Codes and Standards. | The term applicable codes and standards is so general; Air cooler design is based on API 661 7TH EDITION+ ASME VIII div.1+ IPS 245. Please confirm? | Please confirm that TEMA will be followed for the specified parts in this TCL. along others. | TEMA is an standard for shell & tube heat exchangers; however, if you require it for any part of exchanger, please specify which parts? |  | Wherever in this TCL mentioned (ex. Tube to tubesheet joint and tubesheet thk,…) TEMA shall be followed. |  |  |
|  | In case of order, PURCHASER would not review documents sent by VENDOR before receiving VENDOR Print Index and Schedule. VENDOR Print Index and Schedule (VPIS) shall be prepared as first document after PO. All documents shall be issued after getting approval of this mentioned document. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | In case of order, VENDOR should provide her quality control plan (VQCP) based on requirements specified on MR and its attachments and also VENDOR’s experiences and send for approval. PURCHASER’s ITP and relevant specifications attached to MR are minimum requirement and VENDOR should consider them as a base and provide comprehensive Quality Control Plan. | We have not received your ITP./ a sample ITP will be sent. | Noted. |  |  |  |  |  |
|  | Providing Required Facilities for Inspection and Test shall be in VENDOR’s Scope of work. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Utility consumption summary shall be submitted by VENDOR along with his proposal. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All static and dynamic loads on foundations/Steel Structures shall be specified by VENDOR. | Confirmed. But if there is piping load, nozzle loads please provide? | Nozzle loads to be taken into account as the 3 X API. | Confirmed. |  |  |  |  |
|  | All Native files of drawings & calculations (like CodeCalc; FEA; ANSYS; HTRI file; Auto-CAD DWG,..) shall be provided by bidder at detail stage. | Native files will be provided. | Noted. Closed. |  |  |  |  |  |
|  | S.S. Name plates shall be fitted to all machines and equipment, according to project standard DWG. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | VENDOR shall submit the documents which are specified at “BID stage”. Fail to submit the necessary documents will be deemed as offer is disqualified. | Confirmed | Noted. Closed. |  |  |  |  |  |
|  | VENDOR shall confirm that project PMS will be followed for all pipes, valves, gaskets, etc. and also for Tie-in points in battery limit. | As can be seen in project PIDs , battery limit is inlet/outlet nozzles of air cooler; so please clarify if any pipe, valve are in Damafin Scope? | All the inter-connecting pipes and valves, as well as flanges and fittings, and in general all the inter-connecting components to be supplied by vendor, please confirm. | Piping Calculations is noty in Damafin scope, if You want any piping be in Damafin scope, please provide isometric plans; Or if you mean vent & drain interconnecting pipings please clarify? You have 3 different units for each item, each unit has only one bay/bundle; we think there is no interconnecting piping actually, just fluid in one pipe might be distributed between different units. |  |  |  |  |
|  | VENDOR shall consider all required consumable materials for site welding, inspection, tests and etc. of equipment, piping, structures and.... | Consumable material for site welding, inspection, test will be provided. But, it seems that in project PIDs, battery limit is inlet/outlet nozzles of air cooler; so please clarify if any pipe, valve are in Damafin Scope? Because we have assumed that piping is out of Damafin Scope. Damafin battery limit is inlet / outlet nozzles of air cooler, bottom of structure columns, As instrument we have only considered vibration switch, IP Convertor, and LCP. . (LCP as option) Please confirm/clarify? We have not considered any junction box or cable in our scope. Please confirm/clarify? | Only interconnecting connections to be supplied by vendor. (Pipes, Flanges, Fittings,…) | Piping Calculations is noty in Damafin scope, if You want any piping be in Damafin scope, please provide isometric plans; Or if you mean vent & drain interconnecting pipings please clarify? You have 3 different units for each item, each unit has only one bay/bundle; we think there is no interconnecting piping actually, just fluid in one pipe might be distributed between different units. |  |  |  |  |
|  | No fabrication shall be commenced until complete calculations. Shop drawings have been received and approved by purchaser. | Confirmed | Noted. Closed. |  |  |  |  |  |
|  | External supports & attachments, clips for piping (wherever required) shall be supplied by VENDOR. | Insulation support and fire proofing support can be provided. Clips for piping is provided but if it cause loads of piping to be on cooler structure, cost will be announced. It is also mentioned in proposal as option. | As a rule of thumb, considering such clips is in vendor’s scope without any cost impact, please confirm that the matter will be supplied and further cost impact will not be announced. | We don’t have any data on piping load; we have already considered extra weight of structure due to piping load in optional section; but if it changes considerably, it might have cost impact. You might also give us exact piping loads at this stage, then structure weight and price can be calculated exactly. |  | Exact piping load is “3x API”, and to be considered by vendor at this stage. |  |  |
|  | Please confirm that all spare parts (commissioning and two years) shall be sent with the equipment to site at the same time. | Confirmed. They are both considered as option and will be sent at the same time with the equipment. Everything will be based on contract if you require spare parts there and they can be delivered at the same time. | The spare parts should be packed and marked properly before the shipment at vendor’s shop. Packing should be done in accordance with packing and shipping procedure and should be done in a way that the keeping at the ware house will be possible properly. Please confirm. | Confirmed. |  |  |  |  |
|  | Vendor shall provide in his quotation, recommended spare parts list compatible with job specification for commissioning, two years of normal operation and capital spares with unit price and their validity period. Recommended spare parts shall have full description and enough data in accordance with related job specification (PMR & NIOEC-SP-40-03 & Doc. No. E&D-QC-SP-1). | Confirmed. But capital spare parts are not given because we think it is not required. Please clarify what you mean by PMR? Spare parts for commissioning is given based on E&D-QC-SP-1. Spare parts for two years are mentioned in doc 00112O-SP-1. Please confirm/ comment. | PMR is the document handed over as Material Requisition, Spare parts have been clarified on clause No. 39 of Mechanical Section, please provide the mentioned quantities on clause No. 39. | We have tried to give our list for commissioning and two years spare parts, considering clause 39 and all of received documents. As mentioned before our list of Spare parts for commissioning is given based on E&D-QC-SP-1. As mentioned before our list of Spare parts for two years-considering all received documents- are mentioned in doc 00112O-SP-1. We have submitted the list so that you can comment on that because in clause 39, some items are not clear or we think some requested items in documents are not applicable; so please see our lists and comment on it. |  |  |  |  |
|  | Please confirm, any loose items include of electrical & instrument local panel, cables and pipes on battery limit of each equipment will be supplied by vendor. | As can be seen in project PID s, battery limit is inlet/outlet nozzles of air cooler; so please clarify if any pipe, valve are in Damafin Scope? We think that electrical battery limit is not clear in PID. As instrument we have only considered vibration switch, IP Convertor, and LCP. . (LCP as option) Please confirm/clarify? We have not considered any junction box or cable in our scope. Please confirm/clarify? | Inter-connecting piping (If applicable) is in vendor’s scope of work and supply. Please confirm. | Piping Calculations is not in Damafin scope, if You want any piping be in Damafin scope, please provide isometric plans; Or if you mean vent & drain interconnecting pipings please clarify? You have 3 different units for each item, each unit has only one bay/bundle; we think there is no interconnecting piping actually, just fluid in one pipe might be distributed between different units. |  |  |  |  |
|  | For all pressure parts and those required special consideration (such compliance with NACE) as well as for supports the material certificate should be in accordance with EN 10204, 3.1. Material certificate for non-pressure parts shall be in accordance with EN 10204, 2.2. Please confirm. | Confirmed | Noted. Closed. |  |  |  |  |  |
|  | Please confirm that all the attached documents listed in attachment No.1 of the material requisition with Ref. BK-GCS-PEDCO-120-ME-MR-0004_D00 are already in your possession. Some updated documents (latest revision) were handed over with this TCL. | Confirmed | Noted. Closed. |  |  |  |  |  |
| - PROCESS |  |  |  |  |  |  |  |  |
|  | Heat curve shall be input completely in three ISO bar curves. | First Three tabs are considered to be for summer case and the latter three tabs for winter case in each excel file. Please confirm? | Confirmed. |  |  |  |  |  |
|  | Input maximum ambient temperature in thermal file. | Confirmed | Noted. |  |  |  |  |  |
|  | Input minimum ambient temperature in thermal file correctly your input data is not true. | Min ambient temperature is given based on mechanical datasheet. It is more 18.75C in summer case 5 C in winter case. Please confirm? | Min ambient air temperature is 5°C. | Confirmed. |  |  |  |  |
|  | Please don’t fix duty in your thermal files. | Confirmed. Please note that AE-2101 A/B/C datasheet shows two different amount for flowrate. Is it 8864 kg/hr or 8876 kg/hr? Please clarify? | The correct value of flow rate is 8664 kg/hr. | confirmed )for summer case.) |  |  |  |  |
|  | Fan arrangement as per PDS are induced please redesign based on this type arrangement and consider required space for its fans shaft from bundle. | Confirmed | Noted. |  |  |  |  |  |
|  | Please input total tube sheet thickness plus tubes extend from tube sheets in your thermal file based on mechanical consideration and preliminary design and have a good margin for its extra surface. | Confirmed | The designed exchanger has no extra surface (overdesign=0.85%). Please consider an overdesign margin (about 5%). | Confirmed. |  |  |  |  |
|  | Please input plenum chamber type in your thermal file instead of software default. | Confirmed | Noted. Please input plenum height too. | Confirmed. |  |  |  |  |
|  | Please input unfinned tubes lengths in your thermal file based on API. | Confirmed | Un-finned tube length is 90.5 mm which is exceed the API limit. Please recheck (HTRI help) & modify. | Confirmed. |  |  |  |  |
|  | Barometric design pressure is 0.9142 bar. | Confirmed. | Noted. |  |  |  |  |  |
|  | Please design air-cooled with min humidity and fan selection based on maximum humidity. | Confirmed | Noted. |  |  |  |  |  |
|  | Please add and consider all PDS&MDS notes in your design too. | Confirmed | Noted. |  |  |  |  |  |
|  | Total static pressure drop for fan selection shall be total static pressure drop plus 20percent of drop of air across the bundle. | Confirmed | Noted. |  |  |  |  |  |
|  | Please input real material code for tubes selection instead of based material. | Confirmed | Noted. |  |  |  |  |  |
|  | Fins based thickness input data is not correct as per our experience with your company. | Confirmed. It is correct for FPI 10 theses values are correct. | It is about selected base thickness not about FPI | We mean according to Btt spec which our machineries are based on that; for FPI of 10,extruded fin base thickness is 1.2 mm and extruded fin tip thickness is 0.25 mm. This is what our finning machine does in practice. |  | Noted. closed. |  |  |
|  | Please redesign based on new attached heat curve. | Confirmed. | Noted. |  |  |  |  |  |
|  | New comments: - The selected fan diameter is so close to bundle width. Please optimize your design. - For AE-2101, fluid pressure drop is 0.683 bar which is so close to allowable pressure drop. Please consider a little higher margin. - For alternative cases (winter), simulation mode should be selected. - Nozzle material is S.S 316 L, so selected nozzle data base in your file shall be edited and revised. |  |  | 1. Confirmed. 2. 0.651 bar is calculated pressure drop in new design. If not acceptable, Since it is really important in cost of cooler, please specify exactly your required margin for all vendors. 3. Confirmed. 4. Confirmed. |  | Noted. Vendor shall guarantee the number works properly with this margin. |  |  |
| - MECHANIC |  |  |  |  |  |  |  |  |
|  | Following documents shall be submitted; 1.Sub-vendor list 2.Deviation list (project deviation format shall be signed and attached) 3.Quality plan 4.All revised general arrangements based on new thermal design 5.Air cooler estimated weight 6.Delivery plan 7.Reference list | 1. AVL was sent in rev.0 2. Confirmed. 3. Confirmed. 4. Confirmed. 5. Confirmed. Included in proposal. 6. Confirmed. Included in proposal. 7. Confirmed. Included in proposal. | Noted. Closed. |  |  |  |  |  |
|  | Breakdown price of following items shall be included in the proposal, as well as total price. 1) Material and Fabrication for each Section Separately 2) Pre-commissioning & commissioning spare parts (END-QC-SP-1) 3) 2 years operational spare parts (END-QC-SP-1) 4) Packing & transportation 5) Other fee (if any) | 1) Confirmed. 2) confirmed. 3) Two years spare parts are based on 00112O-SP-01. Please confirm. 4) transportation is considered as option. 5) Confirmed. | 3) Spare Parts to be closed at clause No. 39 in mechanical section. | We have tried to give our list for commissioning and two years spare parts , considering clause 39 and all of received documents. As mentioned before our list of Spare parts for commissioning is given based on E&D-QC-SP-1. As mentioned before our list of Spare parts for two years-considering all received documents- are mentioned in doc 00112O-SP-1. We have submitted the list so that you can comment on that because in clause 39, some items are not clear or we think some requested items in documents are not applicable; so please see our lists and comment on it. |  |  |  |  |
|  | Vendor to confirm the project specifications with Ref. BK-GCS-PEDCO-120-ME-SP-0001_D00 and BK-GNRAL-PEDCO-000-ME-SP-0001_D00 are also considered for design of air coolers in addition of ASME Sec. VIII Div.1 and API 661. Also IPS standards IPS-E-PR-785 and IPS-G-ME-245 are to be considered. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Following works to be considered as exclusion of vendor scope; 1.Fire proofing material 2.Permanent gasket and bolt of process nozzle | Confirmed. | Inter connecting bolt and nuts, as well as gaskets and pipes (If required) to be supplied by vendor. Please confirm. | Piping Calculations is noty in Damafin scope, if You want any piping be in Damafin scope, please provide isometric plans; Or if you mean vent & drain interconnecting pipings please clarify? You have 3 different units for each item, each unit has only one bay/bundle; we think there is no interconnecting piping actually, just fluid in one pipe might be distributed between different units. |  |  |  |  |
|  | Following items shall be quoted as option in vendor proposal: 1- Shop & site run in test (including vibration verification) Noted that trial assembly to be included in shop run in test (for one bay per item). 2- Site supervision for installation Please confirm and revise your offer. | 1.Site run test is included and we think shop run test is not needed anymore because site run test is given as option. For trial assembly, it is done in structure manufacturer shop. 2. confirmed./ supervisory is given as option. | Please provide the shop run test optional price in your offer also. | It is already given as you see in optional section of our proposal. |  |  |  |  |
|  | Mechanical guarantee and Guarantee period to be included in BID. | Confirmed. It is already mentioned in 2nd page of proposal. | Noted. Closed. |  |  |  |  |  |
|  | A summary table of air coolers including items No, unit No, Bay No., bundle No., weights and power consumption is needed in vendor proposal. | Confirmed. | The summary table for both winter and summer cases to be reported, moreover, all reported data to be in strict accordance with of thermal calculations and Hirgan Process data sheet. | Confirmed. |  |  |  |  |
|  | Vendor should consider all Mechanical data sheet notes and implement them on their designs and data sheets. | Confirmed | Noted. Closed. |  |  |  |  |  |
|  | Bidder shall confirm to verify nozzle external loads calculations according to API 661 PART 7.1.10 by Finite Element Analysis (nozzle loads shall be used two (3) times of API 661). Please add it as a note in relevant data sheets. | Confirmed. | 3 X API nozzles loads to be taken into consideration, please confirm. | Confirmed |  |  |  |  |
|  | Vendor shall consider bundle expansion on structure. | Confirmed. | Consequently, sliding pad on the sliding header to be provided by vendor, its material and characteristics to be the same as project specifications / reference standards, sliding header to be considered oppose to the front header (Where the nozzles located), please confirm. | Confirmed |  |  |  |  |
|  | Possibility of lateral header movement to be considered by vendor. | Confirmed. | Mechanical calculations for lateral force to be also done. | Confirmed |  |  |  |  |
|  | Requirements of Expanded tube to tube sheet joint, No. of grooves should be followed as per clauses 9.3.2, 9.3.3 of API 661 and TEMA Class R requirements. As regards special services like H2S, lethal and hydrogen services strength welding is required. | Confirmed./ Service Is sour but since in mechanical datasheets, strength welding is required, it is included in the offer for both items. | Noted. Closed. |  |  |  |  |  |
|  | Tube hole diameters, tolerances, grooving and finish shall be in accordance with TEMA Class R. Tubes shall be expanded into the tube sheet up to within 3mm (1/8") of the airside face of the tube sheet. Minimum tube sheet thickness shall be 25 mm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | The minimum thickness of tube sheets and plug sheets in case of plug type headers and removable cover plate headers shall be in accordance with TEMA standard but shall not be less than 25mm including corrosion allowance. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | On the side frames there shall be lugs for lifting the bundles stiffly welded to the side members and with a hole of 25 mm minimum. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Fan guards for air coolers shall be furnished to provide personnel protection during operation. | Confirmed. | Air seal to be provided on bundle in order not to let the air flows from the hollow spaces. | Confirmed |  |  |  |  |
|  | No carbon steel parts to be welded shall have a carbon content higher than 0.25%. please confirm. | Confirmed. No carbon steel part is welded. | Noted. Closed. |  |  |  |  |  |
|  | Material requirement should be in compliance with NACE MR 0175/ISO 15156 and Technical Specification for Material Requirements in Sour Service Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0008. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Corrosion allowance shall be multiplied by two for pass partition plates or stiffeners. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All header flanges shall be welding neck type. Vent and drain nozzle shall be 2” LWN type with ASME rating flange and blinded. All nozzles smaller than 2” to be LWN. Please confirm and revise your technical offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Hydrostatic test shall be in accordance with the requirements of ASME code Sec. VIII Div.1. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All butt welds in headers shall be examined by full RT. All corners welds shall be full UT. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Fan rings, Fan deck, Plenum, walkway grating including boltings shall be hot dip galvanized | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Material of louver blades (if required) shall be high quality galvanized carbon steel. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | TI/PI and vent and drain nozzle sizes shall be specified in relevant data sheet. | No TI, PI is specified in datasheets. But they are mentioned in specification for air cooled heat exchangers 7.1.9.13 & 7.1.9.14. Please clarify if TI, PI is not needed based on process datasheet? Vent & drain are considered based on mechanical datasheets. | PI and TI are required, they should be flange type also. | Confirmed. |  |  |  |  |
|  | Fan performance curves for all fans shall be included to relevant data sheet in quotation. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Bidder to clarify mechanical efficiency of separate power transmissions Em value and related reference. | It is 98% ( from manufacturer) | Noted. Please put it in your offer’s data sheet. | Confirmed. |  |  |  |  |
|  | Access Platform, Maintenance Platform (if required) and Ladders for access to platforms and platform’s gratings are in vendor scope of supply. please confirm Access Platform: Shall be provided on all the four sides. Maintenance Platform : Full steel platform duly interconnected along full length and width of air coolers for fan/motors etc. | Confirmed./ Maintenance platform is required if TOS height that we have considered to be ground clearance from below bundle be 5.5 m. please clarify in row D.4? |  | In this offer it is 5.5 m and maintenance walkway, header walkways and connecting walkways are considered. (walkways on four sides.) |  |  |  |  |
|  | Platforms shall be a minimum of 750 mm wide and 2 m headroom. Design load of platforms shall be 500 kg/m^2. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | The effect of the pipe supports loads on your structure shall be borne by your side without cost impact according to your experience. just the additional price for pipe support steel structure weight can be paid. | It is given in row 5 of optional section in our proposal. If the value of loads which you specify later be far from our assumption, it might have cost impact. | Noted. 3x API loads shall be considered. | Confirmed. |  |  |  |  |
|  | For gasket material and relevant flange specification of blinded flanges, vendor shall follow Piping material specification. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | A vibration switch shall be provided one per motor for each bay within the equipment. The mounting location shall be carefully selected to represent high vibration / trip in case of bearing / fan damage and ease of maintenance. | Confirmed. | Vibration switch type and locations to be clearly shown on the GA. Drawing. Please confirm. | Confirmed. It will be shown in GAD after contract. |  |  |  |  |
|  | Motors electrical area classification and service factor shall be specified. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Minimum stock thickness for extruded fins shall be 0.40 mm. This thickness shall apply at the root of the fin. Fins Stock thickness shall be specified in related data sheet. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | The maximum allowable number of fins is 400 per meter of the tube length. In order to prevent fouling, fin surfaces shall be smooth. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | The width of the tube bundle shall be chosen with due regard to transport and handling aspects, and shall not, in general, exceed 3 meters. At least one inlet nozzle is required per meter of bundle width. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Spare part for commission and 2 years are included at scope of supply and not as optional. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Please confirm to consider the following items in spare parts for pre-commissioning, commissioning and start-up in the scope of supply. Plug: 10% Plug gaskets: 10% (min. 2 sets). Standard bearing: minimum 20% per size and type and material Gaskets for blind nozzles: 100% (min. one set of gasket per each type) Stud bolts & nuts & washer : 5% (min. 2 sets). | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Please confirm to consider the following items in spare parts for 2 years operation in the scope of supply. Plugs Steel 1% & Nonferrous 2% (minimum one number) Plug gasket 5% (minimum one number) Tube support 10% (minimum one number) Gaskets for blind nozzles: 200% (min. two set of gasket per each type) Stud bolts & nuts & washer : 10% (min. 2 sets). The following items as per project requirements attached to MR. Blade Bearings Belts Bolting for Structure Fan Blades Vibration Detectors | Spare parts for two years are mentioned according to doc 00112O-SP-1. Please confirm. | Noted. Spare parts shall consider as project requirement attached to MR. | We have tried to give our list for commissioning and two years spare parts, considering clause 39 and all of received documents. As mentioned before our list of Spare parts for commissioning is given based on E&D-QC-SP-1. As mentioned before our list of Spare parts for two years-considering all received documents- are mentioned in doc 00112O-SP-1. We have submitted the list so that you can comment on that because in clause 39, some items are not clear or we think some requested items in documents are not applicable; so please see our lists and comment on it. |  |  |  |  |
|  | Please confirm to consider the following items in Special tools in the scope of supply as minimum. 1-Level Gauge for Pitch Angle Setting of Fan Blades 2-Torque Wrench for Fan Blade Setting Bolts 3-Torque Wrench for Header Plugs | Confirmed. Level Gauge for Pitch Angle Setting of Fan Blades is actually clinometer. | Noted. Closed. |  |  |  |  |  |
|  | Preservation (N2 purging) shall be considered in vendor scope of supply / work. Please reconfirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All plates used in sour service shall be examined by ultrasonic test for lamination, please confirm compliance. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Belt drivers shall be anti-static, Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | All driver, fans, bearings shall be waterproof for outdoor installation. Please confirm. | Confirmed. |  |  |  |  |  |  |
|  | Earth lugs is in vendor scope of supply shall be considered, Please revise your offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Rotor shaft power at API point shall be specified at all fan characteristics and fan performance curves. Please revise your offer accordingly. | Confirmed./ After P.O. | Noted. Closed. |  |  |  |  |  |
|  | Structure surface preparation and coating shall be hot deep galvanized (ASTM A123). Please confirm and revise offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Fan hub shall be hot deep galvanized. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Air humidity to be corrected in fan data sheet. Worse case humidity shall be considered in fan calculation.(100%). | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Half of fans (50%) shall be equipped with variable pitch automatic system to control fluid temperature, please revise offer accordingly. Related data sheet for fan. This price shall be included SS 316 Tube fitting, actuators, positioner, IP convertor and all necessary parts for pneumatic circuit. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Draft type of fans is induced, Please revise offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Plug gasket to be solid metal. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | The last pass of tubes shall be 1% slope. Please revise your offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Blade material shall be aluminum not GRP. Please revise offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Tube to tube sheet joints shall be revise as per MDS. Please confirm and revise your offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | Flange rating shall be revise as per MDS, Please revise your offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |  |  |
|  | New item: Thermal calculation and results shall be reported in technical proposal. |  |  | Confirmed. |  |  |  |  |
|  | New item: Minimum ambient temperature is different from Hirgan’s data sheet. Please revise. |  |  | Modified./ Confirmed. |  |  |  |  |
|  | New item: Attached form to be filled out. |  |  | Confirmed. |  |  |  |  |
| - PIPING & MATERIAL |  |  |  |  |  |  |  |  |
|  | G.A Drawing (Detail Drawing) of Equipment shall be submitted by vendor after PO. | Confirmed. | Closed. |  |  |  |  |  |
|  | In Vendor Data Sheet in page 4 of 4, for AE-2102 rating of nozzles shall be 600#. | Confirmed. | This comment shall be modified and submitted in new vendor Data Sheet. | It is 600# in new datasheet and in previous datasheet also for AE-2102. Please clarify? |  |  |  |  |
|  | In Vendor Drawing, both Inlet & Outlet nozzles shall be in one end of Air Cooler. | Confirmed. | This comment shall be modified and submitted in new vendor Outline Drawing. | Confirmed. |  |  |  |  |
|  | In Vendor Drawing, Elevation of TOS (Top of Structure) will be at least 5.5 meter. | Confirmed . We have considered elevation of below bundle to be 5.5 m. Since it is ,more than normal, please confirm what you mean exactly ? do you mean ground clearance from below bundle? | It is ok in your new Outline Drawing Rev.1. But please note that this elevation will be finalized after P.O when receiving vendor Detail Drawing. | If it changes considerably, it might have cost impact. |  |  |  |  |
|  | VENDOR shall specify maximum allowable forces and moments at the nozzles for review and purchaser approval. In case of unavoidable over loaded at the nozzles, then the loads should be submitted to the VENDOR for consideration and approval. | (nozzle loads shall be used two (3) times of API 661) Based on row C-9 of this TCL. | Allowable Nozzle Loads shall be considered 3 times of API 661. | Confirmed. |  |  |  |  |
|  | Materials should be as follow: Louver material: SA-283 Gr. C (hot dip galvanized) Plug Material: SA-182 F316L Gasket Material: S.S. 316L | Confirmed/ Or equivalent for louver Confirmed. Confirmed. | Closed. |  |  |  |  |  |
|  | Surface preparation & coating shall be acc. to "Specification for Painting" with Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006. | Confirmed. | Closed. |  |  |  |  |  |
| - INSTRUMENT & CONTROL |  |  |  |  |  |  |  |  |
|  | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0004 for package control type.( for this package Type B only Electrical LCP is required). Signals from Vibration switch and signal to I/p Converter shall be transferred to planed ESD/DCS). VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | We have not recieved BK-GNRAL-PEDCO-000-IN-SP-0004; please send. LCP is considered as option. It only consists of what is shown in PID. For better clarification send BK-GNRAL-PEDCO-000-IN-SP-0004 | Electrical LCP is required for local stop / stop command. | Confirmed./ we consider it as main./ We don’t have BK-GNRAL-PEDCO-000-IN-SP-0004; if it’s really needed, please resend. |  |  |  |  |
|  | Regarding supplying instrument on datasheet), bidder is requested to consider all instruments mentioned on project datasheet. VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0001 for instrumentation devices and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list | Confirmed/ We follow BK-GNRAL-PEDCO-000-IN-SP-0001 for those instruments which are in our scope based on MR and DSH. We think that electrical battery limit is not clear in PID. As instrument we have only considered vibration switch, IP Convertor, and LCP. (LCP as option) Please confirm/clarify? We have not considered any junction box or cable in our scope. Please confirm/clarify? | Specification for switch: •The switches shall be EExd, IIB T4 and the weatherproof requirements of IP-65 as per IEC-60529. •Switch element shall be of the micro switch snap action type and hermetically sealed. Micro-switches shall be two double pole double throw (DPDT) type •The switch contact rating shall be 110VAC @10Amp. •Repeatability shall be ±1% or better of full scale •The accuracy of the pressure switch assembly shall be at least 1% of the span | Micro switch snap action type and hermetically sealed are pressure switch requirements; which we think is not applicable. Also it is mentioned that The accuracy of the pressure switch assembly shall be at least 1% of the span but we think pressure switch is not applicable here; please confirm. Other explanations for vibration switch are confirmed. |  |  |  |  |
|  | - VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0010 for cables and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | We have not considered any junction box or cable in our scope since you have mentioned in row E.7 below that cable from instrument to control/electrical building is by contractor. Please confirm/clarify? | See reply to item 7 |  |  |  |  |  |
|  | Instrument selection, connection & cabling (including vibration switches, I/P converters and 50% fans controlling devices) shall be acc. to "Specification For Instrumentation" Doc. No. BK-GNRAL-PEDCO-000-IN-SP-0001 | Confirmed for these instruments but We have not considered any junction box or cable in our scope. Please confirm/clarify? | Closed |  |  |  |  |  |
|  | All terminals shall be screw type. VENDOR shall note that each core/pair/etc. of cable shall be wired to dedicated terminal | We have not considered any junction box or cable in our scope. So it is NA. | Closed |  |  |  |  |  |
|  | VENDOR shall specify the estimated power required (non-UPS and UPS) | Utility consumption list will be attached. UPS is not applicable. | Closed |  |  |  |  |  |
|  | Cable from LCP/Instruments to Control/Electrical building is by contractor except for special cables( if it is not as per our specifications) which shall be supplied by vendor. | Please clarify what you mean by special cable? We have not considered any cabling in damafin scope in current offer please clarify? | Cable for 24VDC from vibration switch also control cable for 4-20mA from variable pitch I/P convertor to control room is by contractor. If there is any other cable or if above mentioned devices signals are different, cable shall be provided by vendor. | According to G.14, Cable is in client scope. So Damafin has not considered any cable in his offer. |  |  |  |  |
|  | 50% of fans shall be AV type. All required accessories to be considered. | Confirmed. | Closed |  |  |  |  |  |
|  | Vibration switch to be (EExd,IIB,T4, IP65, suitable for 110V@1A rating with 24VDC signal ), please confirm. | 110 V is not normal. Please clarify? | As per project specification switch shall be designed to be worked on 110V@10A rating but normal voltage range is 24VDC. | Based on switch catalogue, possible Switch contacts rating are: 15A, 125 VAC, 250VAC, 480 VAC; 1/8 HP 125 VAC 1/4 HP 250 VAC; 1/2 A, 125VDC; 1/4A,250VDC; 1.5A, 8VDC, 14 VDC, 30VDC; We think 110V is not correct. |  |  |  |  |
|  | New comments: Please find the comments on the attached offer, Rev.01 |  |  |  |  |  |  |  |
| - SAFETY |  |  |  |  |  |  |  |  |
|  | All electrical equipment shall be certified for Zone IIB, T3. | Confirmed. | Closed. |  |  |  |  |  |
|  | The sound pressure level anywhere in the work area shall not exceed 85 dBA. | Confirmed. | Closed. |  |  |  |  |  |
| - ELECTRICAL |  |  |  |  |  |  |  |  |
|  | Electrical system scope of work shall be clarified by vendor & any deviation shall be reported. | Confirmed/We think that electrical battery limit is not clear in PID. As instrument we have only considered vibration switch, IP Convertor, and LCP. (LCP as option) Please confirm/clarify? We have not considered any junction box or cable in our scope. Please confirm/clarify? | LCS is in client scope of work. |  |  |  |  |  |
|  | Vendor list & sub vendor list of manufacture shall be according to project AVL. | Please send AVL. | Closed. |  |  |  |  |  |
|  | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. (IPS-E-EL-100) | Confirmed. | Closed. |  |  |  |  |  |
|  | Motor shall be manufactured & tested in accordance with the latest applicable sections of the IEC standards. Project specification shall be applied as well. | Confirmed. (latest available IEC standard) | Closed. |  |  |  |  |  |
|  | Environmental criteria for design of electrical systems that shall be considered by vendor (According to Electrical System Design Criteria) | Confirmed/. Please send HSE Plan or Hazardous area classification | Closed. |  |  |  |  |  |
|  | Hazard Area classification, Gas group and temperature class of motor shall be at least Exd, IIB, T3, with protection degree of IP54 for motor enclosure and IP55 for terminal box. | Confirmed. | Closed. |  |  |  |  |  |
|  | All accessories related to cable entry/termination in electrical equipment (motors, JBs, etc.) such as cable glands & etc. shall be supplied by vendor. | Cable gland is given. | Closed. |  |  |  |  |  |
|  | 2 temperature detector (RTD) for each winding & 1 one RTD for each bearing should be provided for MV motor | NA | Closed. |  |  |  |  |  |
|  | Load list shall include all motor & non-motor (if there is). For motors, Mechanical power (BHP), Rated power, efficiency, power factor and rated current shall be specified in the proposal. | Motor datasheet is attached. A more complete DS will be submitted after motor purchase. | Closed. |  |  |  |  |  |
|  | API factor, effect of ambient condition especially de-rate factor for altitude shall be considered for specifying rated power of motor and procedure of obtaining rated power of motor from BHP shall be cleared in the proposal. | Based on API 661 7.2.7.1.2 For electric motor drivers, the minimum required driver rated shaft power (Pdr) shall be calculated as follows: Pdr 1.05 (Pf1/Em) Pdr 1.10 (Pf2) where Pdr is driver rated shaft power; Pf1 is fan shaft power operating at specified minimum design temperature with blade angle set for design dry-bulb temperature; Em is mechanical efficiency of the power transmissions; Pf2 is fan shaft power operating at design dry-bulb temperature | calculation will be checked after PO, but motor sizing shall satisfy all requirement. | Confirmed. |  |  |  |  |
|  | A complete set of spare parts for commissioning shall be supplied for each motor. | Two years spare part for motor is given based on document Doc. No. E&D-QC-SP-1. Based on this document no spare part is needed for commissioning for motors. | Closed. |  |  |  |  |  |
|  | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | Site run test is included and we think shop run test is not needed anymore because site run test is given as option as mentioned in on row C5. For trial assembly, it is done in structure manufacturer shop. | Closed. |  |  |  |  |  |
|  | Supplier shall design the routing of the power & control cable inside package. | Confirmed. | Closed. |  |  |  |  |  |
|  | Supply of cables between Junction boxes and Package control panel is in vendor scope of work. In other word, All cabling listed in “Customer cable table” shall be supplied and connected by customer/contractor. Cables shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0014”. | Please clarify what you mean by Package control panel? Do you mean DCS? Do you mean that only cable from instrument JB to package control panel is in damafin scope? Previously, you have mentioned that Cable from Instruments to Control/Electrical building is by contractor. JB is also an instrument so please clarify? Where is this customer cable table? Please refer to document? We have not received BK-GNRAL-PEDCO-000-EL-SP-0014. It should be noted that we didn’t consider any cabling in this offer because we didn’t understand this row. So please clarify? | Cable & LCS are in client scope of work. | Based on row E.1: Electrical LCP is required for local stop / stop command. Do you mean that LCP for local stop/start will be supplied by Client? |  |  |  |  |
|  | If UPS & batteries are required, vendor shall provide all necessary documents (such as calculation, list etc.) & supply required equipment according to purchaser standards. | UPS and batteries are not applicable. | Closed. |  |  |  |  |  |
|  | According to Project Electrical Load List, there are 12 number of Aircooler Fan since in page 1 of Offer, there are only 6 numbers of fans. Vendor load list shall be revised. Project Load List has been attached to document file. | There are 6 Air Coolers, and each air cooler consists of 1 bay with 2 fans. So there are totally 12 fans. | Closed. |  |  |  |  |  |
| - CIVIL & STRUCTURE |  |  |  |  |  |  |  |  |
|  | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2. also according to ASCE 7 (2010) Seismic Zone is equal to Zone 3 with Seismic Importance Factor 1.25 . Besides according to INBC-Part 6 amount of Wind Speed shall be considered 120 Km/hr. It is necessary to consider the above in the data sheets. | Confirmed. | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2 with specific gravity 0.3. Besides, based on ASCE 7-2010 soil is considered in class D. Please consider below parameters in your calculations: Ss = 1.25 S1 = 0.58 Site Coefficient Fa =1.0 Site Coefficient Fv =1.5 SMS=Fa SS SM1=FV S1 PGA = 0.3 Site Coefficient FPGA = 1.2 SDS =0.83 SD1 =0.58 | Confirmed. |  |  |  |  |
|  | New comments: Please find the comments on the attached offer, Rev.01 |  |  |  |  |  |  |  |