| Item No. | Clarification Description(Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- |
| - GENERAL |  |  |  |  |  |  |
|  | VENDOR shall confirm his full compliance to meet purchaser’s specifications, code and standard listed in specifications and mechanical data sheets, PIDs, Plot Plans and etc. Any deviations which not mentioned in deviation list will not be accepted by purchaser at detail stage. If there is not any Deviation or Exception from purchaser’s technical documents, VENDOR shall be signed with "NO DEVIATION" and submitted with his proposal. | Confirmed. Confirm. Be informed that deviation form will be submitted after finalizing technical points in this TCL. | Noted. Will be closed after finalizing technical points and submitting deviations. |  |  |  |
|  | VENDOR is sole responsible to consider this clarification and modify his offer based on this TCL. All modifications which need to be considered on the next revision of offer based on this clarification should be clearly marked with revision and cloud marks. All consequences due to changes without cloud mark are in VENDOR’s responsibility. Anyway, this clarification has priority over the offer. | Confirmed. | Noted. Closed. |  |  |  |
|  | The VENDOR shall have overall responsibility for the coordination with his Sub-Vendors, and for the proper execution of any accessory item assembly, testing, delivery and any other service defined herein. | Confirmed. | Noted. Closed. |  |  |  |
|  | All equipment shall be designed to meet the requirements shown in the Project Specification and data sheets. | Confirmed. | Noted. Closed. |  |  |  |
|  | All documents required after purchase order shall be submitted in accordance with VENDOR documents requirements of the PMR. | Confirmed. If applicable | Noted. Closed. |  |  |  |
|  | All required special tools shall be considered in VENDOR main offer (they shall be supplied by bidder without any cost impact). A qualified and complete list has to be included in the bid documentation | Confirmed. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to project specification mentioned in PMR. | Confirmed. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm project performance and mechanical guarantee based on data in PMR. | Confirmed. | Noted. Closed. |  |  |  |
|  | VENDOR should confirm that all sub-vendors shall be selected from project Approved Bidder List (A.V.L.). In case of any deviation, bidder shall submit his deviation list for purchaser. Also, VENDOR is fully responsible for his Sub-vendors. | Confirmed, the materials shall be supplied from approved vendor list if possible; otherwise, the sub-vendor will be introduced to achieve client’s approval. | Please submit the sub-vendor list before PO. For client’s approval. | Confirmed. |  |  |
|  | Material specification consists of class and relative grade shall be submitted by detail based on ASME/ ASTM for the whole package. VENDOR shall prepare material and material grade as per data sheets of equipment. Any substitution shall be expressed in deviation form. Meanwhile substitution after Purchase order is not approved. | Confirmed. | Noted. Closed. |  |  |  |
|  | VENDOR to confirm his compliance with documents priority stated in PMR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement. | Confirmed. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm that surface preparation and painting of all equipment material including valves, pipes, fittings and everything within the package are in accordance with project painting specification. | Will be considered in FSK scope of work. The scope is limited to air coolers (flange to flange). | Interconnecting pipe & valves (between bundles & bays) to be supplied by vendor. | Confirmed. Please clarify valve type and details. | Please consider valve and pipes based on your design. |  |
|  | PURCHASER’s approval shall in no way be construed as relieving VENDOR of any of his obligation, responsibilities or liabilities under the CONTRACT and/or applicable Codes and Standards. | Confirmed. | Noted. Closed. |  |  |  |
|  | In case of order, PURCHASER would not review documents sent by VENDOR before receiving VENDOR Print Index and Schedule. VENDOR Print Index and Schedule (VPIS) shall be prepared as first document after PO. All documents shall be issued after getting approval of this mentioned document. | Confirmed. | Noted. Closed. |  |  |  |
|  | In case of order, VENDOR should provide her quality control plan (VQCP) based on requirements specified on MR and its attachments and also VENDOR’s experiences and send for approval. PURCHASER’s ITP and relevant specifications attached to MR are minimum requirement and VENDOR should consider them as a base and provide comprehensive Quality Control Plan. | Will be provided after PO. | Noted. Closed |  |  |  |
|  | Providing Required Facilities for Inspection and Test shall be in VENDOR’s Scope of work. | Confirmed. Where applicable | Noted. Closed. |  |  |  |
|  | Utility consumption summary shall be submitted by VENDOR along with his proposal. | Confirmed. (Motor power consumption is provided in technical offer) | Noted. Closed. |  |  |  |
|  | All static and dynamic loads on foundations/Steel Structures shall be specified by VENDOR. | Confirm, it will be provided after PO. | Noted. Closed. |  |  |  |
|  | All Native files of drawings & calculations (like CodeCalc; FEA; ANSYS; HTRI file; Auto-CAD DWG,..) shall be provided by bidder at detail stage. | Confirmed. It will be submitted during detail design. | Noted. |  |  |  |
|  | S.S. Name plates shall be fitted to all machines and equipment, according to project standard DWG. | Confirmed. | Noted. Closed. |  |  |  |
|  | VENDOR shall submit the documents which are specified at “BID stage”. Fail to submit the necessary documents will be deemed as offer is disqualified. | Confirmed. | Noted. Closed. |  |  |  |
|  | VENDOR shall confirm that project PMS will be followed for all pipes, valves, gaskets, etc. and also for Tie-in points in battery limit. | Confirmed. However, air cooler battery limit (flange to flange) has been considered as Tie-in Point. | All the inter-connecting pipes and valves, as well as flanges and fittings, and in general all the inter-connecting components to be supplied by vendor, please confirm. | Confirmed. Please clarify valve type and details. | Please consider valve and pipes based on your design. |  |
|  | VENDOR shall consider all required consumable materials for site welding, inspection, tests and etc. of equipment, piping, structures and.... | Confirmed. | Noted. Closed. |  |  |  |
|  | No fabrication shall be commenced until complete calculations. Shop drawings have been received and approved by purchaser. | Confirmed. | Noted. Closed. |  |  |  |
|  | External supports & attachments, clips for piping (wherever required) shall be supplied by VENDOR. | Confirmed, where applicable. | Noted. Closed. |  |  |  |
|  | Please confirm that all spare parts (commissioning and two years) shall be sent with the equipment to site at the same time. | Confirmed. | The spare parts should be packed and marked properly before the shipment at vendor’s shop. Packing should be done in accordance with packing and shipping procedure and should be done in a way that the keeping at the ware house will be possible properly. Please confirm. | Confirmed. |  |  |
|  | Vendor shall provide in his quotation, recommended spare parts list compatible with job specification for commissioning, two years of normal operation and capital spares with unit price and their validity period. Recommended spare parts shall have full description and enough data in accordance with related job specification (PMR & NIOEC-SP-40-03 & Doc. No. E&D-QC-SP-1). | Confirmed. | Noted. Closed. |  |  |  |
|  | Please confirm, any loose items include of electrical & instrument local panel, cables and pipes on battery limit of each equipment will be supplied by vendor. | All instruments such as power cables, local panel and piping are out of Vendor’s scope of work. (Except vibration switch) | Noted. However, Inter-connecting piping (If applicable) is in vendor’s scope of work and supply. Please confirm. | Confirmed. |  |  |
|  | For all pressure parts and those required special consideration (such compliance with NACE) as well as for supports the material certificate should be in accordance with EN 10204, 3.1. Material certificate for non-pressure parts shall be in accordance with EN 10204, 2.2. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | Please confirm that all the attached documents listed in attachment No.1 of the material requisition with Ref. BK-GCS-PEDCO-120-ME-MR-0004_D00 are already in your possession. Some updated documents (latest revision) were handed over with this TCL. | Confirmed. | Noted. Closed. |  |  |  |
| - PROCESS |  |  |  |  |  |  |
|  | Mechanical consideration shall be input in your thermal file same as total tube sheet thickness plus tubes extended from tube sheet. | Confirmed. | Noted. Fan shaft lane width is considered 50 mm. Please recheck is it possible to located fan shaft | Confirmed. Fan shaft lane width has been considered as modified in HTRI. |  |  |
|  | Barometric pressure shall be considered in your thermal input data same as set pressure of heat curve and operating pressure 0.9142 bar. | Confirmed. | Noted. |  |  |  |
|  | Design case shall be run in rating mode and the other case shall be run in simulation mode and reported in your data sheet. | Confirmed. | Noted. |  |  |  |
|  | Plenum chamber type is not box type please edit it in your thermal file. | Confirmed. | Plenum chamber is selected as box type But it is not box type it shall be revised and edited. | Confirmed. Plenum chamber has been considered as transition. |  |  |
|  | Plenum height shall be input in your thermal file. | Confirmed. | Noted. |  |  |  |
|  | Ground clearance shall be input in your thermal file | Confirmed. | Noted. |  |  |  |
|  | Un finned tube length input data shall be followed as per API7.1.11.6. | Confirmed. | Un-finned tube length exceeds API limit for AE-2102.(please used HTRI help for input data) | Confirmed. Please check new HTRI design file. |  |  |
|  | Nozzle material is S.S 316 L ,so selected nozzle data base in your file shall be edited and revised. | Confirmed. | Noted. Nozzle ID selected is not compatible by SS pipe sch. Please recheck. | Confirmed. Please check new HTRI design file. |  |  |
|  | Calculated pressure drop of FSK offer show that the related exchanger sizing is not optimum and shall be revised. | Air coolers have been designed in order to optimize overall aspects. | No action is done. Pressure drop is still far lower than allowable one. | Confirmed. Please check new HTRI design file. |  |  |
|  | Please redesign based on new attached heat curve. | Confirmed. | Noted. |  |  |  |
|  | Please design air-cooled with min humidity and fan selection based on maximum humidity. | Confirmed. | Noted. |  |  |  |
|  | Please add and consider all PDS&MDS notes in your design too. | Confirmed. | Noted. |  |  |  |
|  | Total static pressure drop for fan selection shall be total static pressure drop plus 20percent of drop of air across the bundle. | Confirmed. | Only static pressure drop is considered for fan selection of AE-2101. It shall be modified by addition of 20% of bundle pressure drop. Please consider and edit for all items. | Confirmed. Please check new fan data sheet attachment on technical offer |  |  |
|  | Heat curve shall be input completely in three ISO bar curves. | Confirmed. | Noted. |  |  |  |
|  | New comments: - Max ambient temperature shall be input in thermal files. - Please consider more extra surface in your design (about 5%). |  |  | Confirmed. |  |  |
| - MECHANIC |  |  |  |  |  |  |
|  | Following documents shall be submitted; 1.Reference list 2.Deviation list (project deviation format shall be signed and attached) 3.Quality plan 4.All revised general arrangements based on new thermal design 5.Air cooler estimated weight 6.Delivery plan | 1. Confirmed. 2. Will be provided after closing current TCL. 3. Confirmed. 4. GA will be provided after PO. 5. Confirmed. 6. Preliminary schedule is provided. | Deviation list to be submitted while this TCL. Is going to be closed. |  |  |  |
|  | Breakdown price of following items shall be included in the proposal, as well as total price. 1) Material and Fabrication for each Section Separately 2) Pre-commissioning & commissioning spare parts (END-QC-SP-1) 3) 2 years operational spare parts (END-QC-SP-1) 4) Packing & transportation 5) Other fee (if any) | Will be provided in commercial offer. | Noted. Closed. |  |  |  |
|  | Vendor to confirm the project specifications with Ref. BK-GCS-PEDCO-120-ME-SP-0001_D00 and BK-GNRAL-PEDCO-000-ME-SP-0001_D00 are also considered for design of air coolers in addition of ASME Sec. VIII Div.1 and API 661. Also IPS standards IPS-E-PR-785 and IPS-G-ME-245 are to be considered. | Confirmed. | Noted. Closed. |  |  |  |
|  | Following works to be considered as exclusion of vendor scope; 1.Fire proofing material 2.Permanent gasket and bolt of process nozzle | Confirmed. | Inter connecting bolt and nuts, as well as gaskets and pipes (If required) to be supplied by vendor. Please confirm. | Confirmed. |  |  |
|  | Following items shall be quoted as option in vendor proposal: 1- Shop & site run in test (including vibration verification) Noted that trial assembly to be included in shop run in test (for one bay per item). 2- Site supervision for installation Please confirm and revise your offer. | Confirmed. Please kindly find revised technical offer. | Noted. Closed. |  |  |  |
|  | Mechanical guarantee and Guarantee period to be included in BID. | Confirmed. | Noted. Closed. |  |  |  |
|  | A summary table of air coolers including items No, unit No, Bay No., bundle No., weights and power consumption is needed in vendor proposal. | Confirmed. | Noted. Closed. |  |  |  |
|  | Vendor should consider all Mechanical data sheet notes and implement them on their designs and data sheets. | Confirmed. | Noted. Closed. |  |  |  |
|  | Bidder shall confirm to verify nozzle external loads calculations according to API 661 PART 7.1.10 by Finite Element Analysis (nozzle loads shall be used two (3) times of API 661). Please add it as a note in relevant data sheets. | Please clarify whether 2 or 3 to be considered. | 3 X API nozzles loads to be taken into consideration, please confirm. | Confirmed. |  |  |
|  | Vendor shall consider bundle expansion on structure. | Confirmed | Consequently, sliding pad on the sliding header to be provided by vendor, its material and characteristics to be the same as project specifications / reference standards, sliding header to be considered oppose to the front header (Where the nozzles located), please confirm. | Confirmed. |  |  |
|  | Possibility of lateral header movement to be considered by vendor. | Confirmed. | Mechanical calculations for lateral force to be also done. | Confirmed. |  |  |
|  | Requirements of Expanded tube to tube sheet joint, No. of grooves should be followed as per clauses 9.3.2, 9.3.3 of API 661 and TEMA Class R requirements. As regards special services like H2S, lethal and hydrogen services strength welding is required. | Confirmed. | Noted. Closed. |  |  |  |
|  | Tube hole diameters, tolerances, grooving and finish shall be in accordance with TEMA Class R. Tubes shall be expanded into the tube sheet up to within 3mm (1/8") of the airside face of the tube sheet. Minimum tube sheet thickness shall be 25 mm. | Confirmed. | Expansion length shall not be less than the tube O.D. Please confirm. | Confirmed. |  |  |
|  | The minimum thickness of tube sheets and plug sheets in case of plug type headers and removable cover plate headers shall be in accordance with TEMA standard but shall not be less than 25mm including corrosion allowance. | Confirmed. | Noted. Closed. |  |  |  |
|  | On the side frames there shall be lugs for lifting the bundles stiffly welded to the side members and with a hole of 25 mm minimum. | Confirmed. | Noted. Closed. |  |  |  |
|  | Fan guards for air coolers shall be furnished to provide personnel protection during operation. | Confirmed. | Noted. Closed. |  |  |  |
|  | No carbon steel parts to be welded shall have a carbon content higher than 0.25%. please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | Material requirement should be in compliance with NACE MR 0175/ISO 15156 and Technical Specification for Material Requirements in Sour Service Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0008. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | Corrosion allowance shall be multiplied by two for pass partition plates or stiffeners. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | All header flanges shall be welding neck type. Vent and drain nozzle shall be 2” LWN type with ASME rating flange and blinded. All nozzles smaller than 2” to be LWN. Please confirm and revise your technical offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |
|  | Hydrostatic test shall be in accordance with the requirements of ASME code Sec. VIII Div.1. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | All butt welds in headers shall be examined by full RT. All corners welds shall be full UT. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | Fan rings, Fan deck, Plenum, walkway grating including boltings shall be hot dip galvanized | Confirmed. | Noted. Closed. |  |  |  |
|  | Material of louver blades (if required) shall be high quality galvanized carbon steel. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | TI/PI and vent and drain nozzle sizes shall be specified in relevant data sheet. | TI / PI connections, vent and drain have been considered. | Noted. Closed. |  |  |  |
|  | Fan performance curves for all fans shall be included to relevant data sheet in quotation. | Confirmed. | Noted. Closed. |  |  |  |
|  | Bidder to clarify mechanical efficiency of separate power transmissions Em value and related reference. | Confirmed IE2 or IE3 has been considered. | Noted. Closed. |  |  |  |
|  | Access Platform, Maintenance Platform (if required) and Ladders for access to platforms and platform’s gratings are in vendor scope of supply. please confirm Access Platform: Shall be provided on all the four sides. Maintenance Platform : Full steel platform duly interconnected along full length and width of air coolers for fan/motors etc. | Confirmed. | Noted. Closed. |  |  |  |
|  | Platforms shall be a minimum of 750 mm wide and 2 m headroom. Design load of platforms shall be 500 kg/m^2. | Confirmed. | Noted. Closed. |  |  |  |
|  | The effect of the pipe supports loads on your structure shall be borne by your side without cost impact according to your experience. just the additional price for pipe support steel structure weight can be paid. | The effect of piping load is not considered on main steel structure weight. So, for the accurate estimation, the evaluated piping load shall be submitted at this stage. Otherwise, any extra weight due to piping load shall be considered as unit rate/kg at project stage. | Piping loads can be considered as the triple API values for your estimation, but the actual value of piping loads on the probable pipe supports cannot be evaluated at this stage, it will be provided during detail design stage. | Confirmed. |  |  |
|  | For gasket material and relevant flange specification of blinded flanges, vendor shall follow Piping material specification. | Confirmed. | Gaskets for nozzles shall be spiral wound type, graphite filled with inner ring S.S.316 and outer ring S.S 316. Please confirm. | Confirmed. |  |  |
|  | A vibration switch shall be provided one per motor for each bay within the equipment. The mounting location shall be carefully selected to represent high vibration / trip in case of bearing / fan damage and ease of maintenance. | Confirmed. | Vibration switch type and locations to be clearly shown on the GA. Drawing. Please confirm. | Confirmed. |  |  |
|  | Motors electrical area classification and service factor shall be specified. | Confirmed. | Based on mechanical data sheet, EExd, IIB, T3, (IP 55) shall be considered by vendor. | Confirmed. |  |  |
|  | Minimum stock thickness for extruded fins shall be 0.40 mm. This thickness shall apply at the root of the fin. Fins Stock thickness shall be specified in related data sheet. | Confirmed. | Noted. Closed. |  |  |  |
|  | The maximum allowable number of fins is 400 per meter of the tube length. In order to prevent fouling, fin surfaces shall be smooth. | Confirmed. | Noted. Closed. |  |  |  |
|  | The width of the tube bundle shall be chosen with due regard to transport and handling aspects, and shall not, in general, exceed 3 meters. At least one inlet nozzle is required per meter of bundle width. | Confirmed. | Noted. Closed. |  |  |  |
|  | Spare part for commission and 2 years are included at scope of supply and not as optional. | Confirmed. | Noted. Closed. |  |  |  |
|  | Please confirm to consider the following items in spare parts for pre-commissioning, commissioning and start-up in the scope of supply. Plug: 10% Plug gaskets: 10% (min. 2 sets). Standard bearing: minimum 20% per size and type and material Gaskets for blind nozzles: 100% (min. one set of gasket per each type) Stud bolts & nuts & washer : 5% (min. 2 sets). | Confirmed. | Noted. Closed. |  |  |  |
|  | Please confirm to consider the following items in spare parts for 2 years operation in the scope of supply. Plugs Steel 1% & Nonferrous 2% (minimum one number) Plug gasket 5% (minimum one number) Tube support 10% (minimum one number) Gaskets for blind nozzles: 200% (min. two set of gasket per each type) Stud bolts & nuts & washer: 10% (min. 2 sets). The following items as per project requirements attached to MR. Blade Bearings Belts Fan Blades Bolting for Structure Vibration Detectors | Revised 2 years spare parts has been provided on technical offer based on attached document. Please check and advise. | Noted. Closed. |  |  |  |
|  | Please confirm to consider the following items in Special tools in the scope of supply as minimum. 1-Level Gauge for Pitch Angle Setting of Fan Blades 2-Torque Wrench for Fan Blade Setting Bolts 3-Torque Wrench for Header Plugs | Confirmed. | Noted. Closed. |  |  |  |
|  | Preservation (N2 purging) shall be considered in vendor scope of supply / work. Please reconfirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | All plates used in sour service shall be examined by ultrasonic test for lamination, please confirm compliance. | Confirmed. | Noted. Closed. |  |  |  |
|  | Belt drivers shall be anti-static, Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | All driver, fans, bearings shall be waterproof for outdoor installation. Please confirm. | Confirmed. | IP55 for motor should be considered. Please confirm | Confirmed. |  |  |
|  | Earth lugs is in vendor scope of supply. shall be considered, Please revise your offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |
|  | Rotor shaft power at API point shall be specified at all fan characteristics and fan performance curves. Please revise your offer accordingly. | API point is mentioned on attached Fan Curves. | Noted. Closed. |  |  |  |
|  | Structure surface preparation and coating shall be hot deep galvanized (ASTM A123). Please confirm and revise offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |
|  | Fan hub shall be hot deep galvanized. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | Air humidity to be corrected in fan data sheet. Worse case humidity shall be considered in fan calculation.(100%) | Confirmed. | Noted. Closed. |  |  |  |
|  | Half of fans (50%) shall be equipped with variable pitch automatic system to control fluid temperature, please revise offer accordingly. Related data sheet for fan. This price shall be included SS 316 Tube fitting, actuators, positioner, IP convertor and all necessary parts for pneumatic circuit. Please confirm. | Confirmed. | Noted. The last version of PID is attached. |  |  |  |
|  | Draft type of fans is induced, Please revise offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |
|  | Plug gasket to be solid metal. Please confirm. | Confirmed. | Noted. Closed. |  |  |  |
|  | The last pass of tubes shall be 1% slope. Please revise your offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |
|  | Blade material shall be aluminum not GRP. Please revise offer accordingly. | Confirmed. | Noted. Closed. |  |  |  |
|  | New Item: Nozzle sizes are specified in Hirgan's data sheet and HTRI file and vendor's data sheet are not the same, also, nozzle schedules should be finalized after mechanical design. please correct. |  |  | Confirmed. |  |  |
|  | New Item: In item AE-2101 winter alter case the value of outlet temperature of tubes is not similar to Hirgan’s data sheet. Please remove the discrepancy. |  |  | Will be negotiation in meeting. |  |  |
|  | New item: Bundle layout and exchanger's drawing shall be input in technical offer. please revise. |  |  | Confirmed. |  |  |
|  | New item: Over design in winter cases are negative in HTRI native file. Please revise and correct. |  |  | Will be negotiation in meeting. |  |  |
|  | New item: Attached form to be filled out. |  |  | Confirmed. |  |  |
| - PIPING & MATERIAL |  |  |  |  |  |  |
|  | Preliminary Drawing shall be submitted and Elevation of TOS (Top of Structure) will be at least 5.5 meter. | Confirmed. | Closed. |  |  |  |
|  | In Vendor Drawing, both Inlet & Outlet nozzles shall be in one end of Air Cooler. | Confirmed. | Closed. |  |  |  |
|  | In Vendor Technical Offer in page 26 of 34, for AE-2101 rating of nozzles shall be 300#. | Confirmed. | Closed. |  |  |  |
|  | In Vendor Technical Offer in page 30 of 34, for AE-2102 rating of nozzles shall be 600#. | Confirmed. | Closed. |  |  |  |
|  | VENDOR shall specify maximum allowable forces and moments at the nozzles for review and purchaser approval. In case of unavoidable over loaded at the nozzles, then the loads should be submitted to the VENDOR for consideration and approval. | Confirmed it will be provided after PO. | Closed. |  |  |  |
|  | Surface preparation & coating shall be acc. to "Specification for Painting" with Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006. | Confirmed. | Closed. |  |  |  |
|  | Gasket shall be spiral wound type, graphite filled with inner ring S.S.316 and outer ring S.S 316. | Confirmed. | Closed. |  |  |  |
|  | Louver material should be SA-283 Gr. C. | Based on Vendor’s previous similar experience it is suggested to use ST37 instead. | Data sheet shall be followed. | Confirmed. |  |  |
|  | Structural material should be SA-36 (hot dip galvanized). | Based on Vendor’s previous similar experience it is suggested to use ST37 instead. | Data sheet shall be followed. | Confirmed. |  |  |
| - INSTRUMENT & CONTROL |  |  |  |  |  |  |
|  | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0004 for package control type.( for this package Type B only Electrical LCP is required). Signals from Vibration switch and signal to I/p Converter shall be transferred to plan ESD/DCS). VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Please be noted that all vibration switches will be dry contact type and digital, and I/P convertor are loop power. So electrical LCP is not required. | ELECTRICAL LCP with start / stop push button is required | Confirmed. | As per Electrical Dep. Comment, LCP is provided by contractor VS control signal cable and JB is scope out if VS signal is 24 VDC. I/P control command cable and JB is scope out if signal is 4-20 mA, intrinsically safe. Otherwise if cables are special type vendor shall prepare them. |  |
|  | Regarding supplying instrument on datasheet), bidder is requested to consider all instruments mentioned on project datasheet. VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0001 for instrumentation devices and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list | Confirmed.it will be considered in air cooler battery limit, where applicable. | Closed |  | Specification for switch: •The switches shall be EExd, IIB T4 and the weatherproof requirements of IP-65 as per IEC-60529. •Switch element shall be of the micro switch snap action type and hermetically sealed. Micro-switches shall be two double pole double throw (DPDT) type •The switch contact rating shall be 110VAC @10Amp. •Repeatability shall be ±1% or better of full scale •The accuracy of the pressure switch assembly shall be at least 1% of the span |  |
|  | - VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0010 for cables and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Confirmed, however power cables are out of F.S.K scope of work and supply. Cable between instrument and junction box will be supplied. | Normal Cabling between instrument and JB is by contractor. | Confirmed. |  |  |
|  | Instrument selection, connection & cabling (including vibration switches, I/P converters and 50% fans controlling devices) shall be acc. to "Specification For Instrumentation" Doc. No. BK-GNRAL-PEDCO-000-IN-SP-0001 | Instrument selection as per relevant SPEC is confirmed. Although cable between instrument and junction box will be supplied, but cable connection & cabling is out of FSK scope. | Normal Cabling between instrument and JB is by contractor. | Confirmed. |  |  |
|  | All terminals shall be screw type. VENDOR shall note that each core/pair/etc. of cable shall be wired to dedicated terminal | Confirmed. | Closed |  |  |  |
|  | VENDOR shall specify the estimated power required (non-UPS and UPS) | As all vibration switches will be dry contact type, and I/P convertor are loop power, Power estimation (non-UPS and UPS), is not required. | Closed |  |  |  |
|  | Cable from LCP/Instruments to Control/Electrical building is by contractor except for special cables( if it is not as per our specifications) which shall be supplied by vendor. | All instrument & power cables Is out of F.S.K scope of work and supply. Just Cable between instrument and junction box will be supplied | Normal Cabling between instrument and JB is by contractor. | Confirmed. |  |  |
|  | 50% of fans shall be AV type. All required accessories to be considered. | Confirmed. | Closed |  |  |  |
|  | Vibration switch to be (EExd,IIB,T4, IP65, suitable for 110V@1A rating with 24VDC signal ), please confirm. | EExd IIB +H2 T3 is suggested. Contact rating will be 15A @ 125-480 Vac. Vibration switches will be digital type. | Closed |  |  |  |
|  | New comments: Please find the comments on the attached offer, Rev.01. |  |  | Confirmed. |  |  |
| - SAFETY |  |  |  |  |  |  |
|  | All electrical equipment shall be certified for Zone IIB, T3. | Confirmed. | Closed. |  |  |  |
|  | The sound pressure level anywhere in the work area shall not exceed 85 dBA. | Confirmed. | Closed. |  |  |  |
| - ELECTRICAL |  |  |  |  |  |  |
|  | Electrical system scope of work shall be clarified by vendor & any deviation shall be reported. | Confirmed. | Closed. |  |  |  |
|  | Vendor list & sub vendor list of manufacture shall be according to project AVL. | Confirmed. | Closed. |  |  |  |
|  | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. (IPS-E-EL-100) | Confirmed. | Closed. |  |  |  |
|  | Motor shall be manufactured & tested in accordance with the latest applicable sections of the IEC standards. Project specification shall be applied as well. | Confirmed. | Closed. |  |  |  |
|  | Environmental criteria for design of electrical systems that shall be considered by vendor (According to Electrical System Design Criteria) | Confirmed. | Closed. |  |  |  |
|  | Hazard Area classification, Gas group and temperature class of motor shall be at least Exd, IIB, T3, with protection degree of IP54 for motor enclosure and IP55 for terminal box. | Confirmed. Exd has been considered. | Closed. |  |  |  |
|  | All accessories related to cable entry/termination in electrical equipment (motors, JBs, etc.) such as cable glands & etc. shall be supplied by vendor. | Cable glands and accessories will be supplied | Closed. |  |  |  |
|  | Load list shall include all motor & non-motor (if there is). For motors, Mechanical power (BHP), Rated power, efficiency, power factor and rated current shall be specified in the proposal. | Confirmed. | Closed. |  |  |  |
|  | API factor, effect of ambient condition especially de-rate factor for altitude shall be considered for specifying rated power of motor and procedure of obtaining rated power of motor from BHP shall be cleared in the proposal. | Confirmed. | Closed. |  |  |  |
|  | A complete set of spare parts for commissioning shall be supplied for each motor. | Confirmed. | Closed. |  |  |  |
|  | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | Confirmed | Closed. |  |  |  |
|  | Supplier shall design the routing of the power & control cable inside package. | Cable route drawing will be submitted however supply of power & control cable, tray and ladders are out of scope. | Closed. |  |  |  |
|  | Supply of cables between Junction boxes and Package control panel is in vendor scope of work. In other word, All cabling listed in “Customer cable table” shall be supplied and connected by customer/contractor. Cables shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0014”. | Supply of power & control cable, tray and ladders are out of scope. | Closed. |  |  |  |
|  | If UPS & batteries are required, vendor shall provide all necessary documents (such as calculation, list etc.) & supply required equipment according to purchaser standards. | UPS & batteries is out of scope. Electrical load list will be submitted. | Closed. |  |  |  |
|  | According to Project Electrical Load List, there are 12 number of Air cooler Fans. Vendor load list shall be Issued. Project Load List has been attached to document file. | Confirmed. | Closed. |  |  |  |
|  | LCS in not in vendor scope of work. Client will supply LCSs for start & stop of electrical motors. |  |  |  |  |  |
| - CIVIL & STRUCTURE |  |  |  |  |  |  |
|  | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2. also according to ASCE 7 (2010) Seismic Zone is equal to Zone 3 with Seismic Importance Factor 1.25 . Besides according to INBC-Part 6 amount of Wind Speed shall be considered 120 Km/hr. It is necessary to consider the above in the data sheets. | Confirmed. | Based on STD2800 this site is located at High Risk Area which is named Seismic Zone 2 with specific gravity 0.3. Besides, based on ASCE 7-2010 soil is considered in class D. Please consider below parameters in your calculations: Ss = 1.25 S1 = 0.58 Site Coefficient Fa =1.0 Site Coefficient Fv =1.5 SMS=Fa SS SM1=FV S1 PGA = 0.3 Site Coefficient FPGA = 1.2 SDS =0.83 SD1 =0.58 | Confirmed. |  |  |