## Sheet 1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-SA-CN-0002_D02 |  |  |  |  | EPC Contractor Tr. No : BK-HD-PEDCO-T-0985 |  |  | Transmital Date:22/MAY/2022
Document Title: Calculation Note For Fire Water Demand |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-SF-TR-0985 |  |  | Transmital Date:22/MAY/2022
[5 empty] | CRS No:NISOC- CRS-BK-GCS-PEDCO-120-SA-CN-0002_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | اتصالات لازم جهت پر کردن مخازن آب آتش نشانی در مواقع اضطراری با تانکر پیش بینی شود. |  | 1401-2294-165031 | 1401/05/11 | در مدارک PFD و P&ID بررسی و در نظر گرفته می شود.
2 | لازم است pressure sensing line بر اساس NFPA 20 اصلاح شود. |  | 1401-2294-165031 | 1401/05/11 | در مدارک PFD و P&ID بررسی و در نظر گرفته می شود.
3 | نقاط تنظیم پمپ ها بر اساس نقه نظرات قبلی این امور اصلاح گردد. |  | 1401-2294-165031 | 1401/05/11 | در مدارک PFD و P&ID بررسی و در نظر گرفته می شود.
4 | در قسمت Note به بند 4,20,1,2 استاندارد NFPA 20 در خصوص عدم لحاظ نمودن PCV بر روی خط هدر اشاره گردد. |  | 1401-2294-165031 | 1401/05/11 | در مدارک PFD و P&ID بررسی و در نظر گرفته می شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: