## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 10
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | DT | 0006 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | AUG.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | JUN.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAR.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class: 2 |  |  |  | Client Doc. Number: F9Z-707976
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 10
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | DT | 0006 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 | X | X | X | [5 empty] | 73
10 | X | X | X | [5 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 10
9184 – 073 - 053 |  |  | BK | W007S | PEDCO | 110 | IN | DT |  | 0006 | D02
REFERENCE DOCUMENTS :
| Specification For Instrumentation | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| Process Basis Of Design | [7 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| P&ID - Extension of Binak B/C Manifold | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| Piping Material Specification | [7 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
| Instrument & Control System Design Criteria | [7 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
| Process Flow Diagram - Extension of Binak B/C Manifold | [7 empty] | BK-W007S-PEDCO-110-PR-PF-0001
| Specification for Control Valve | [7 empty] | BK-GNRAL-PEDCO-000-IN-SP-0005
| Process Design Criteria | [7 empty] | BK-GNRAL-PEDCO-000-PR-DC-0001

## Note
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 10
9184 – 073 - 053 |  |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0006 | D02
GENERAL NOTES:
1-The electrical equipment shall be suitable for hazardous area Zone 2, gas group IIB, temperature class T4.
2-Flow direction shall be specified on the valve body.
3- All flanges shall be in accordance with ASME B16.5.
4- Each valve shall be furnished with name plate as per "specification for control valves" with No. "BK-GNRAL-PEDCO-000-IN-SP-0005".
5- The following items shall be considered:
Design standard for globe valves: IPS-M-IN-160, BS1873
Design standard for plug valves: IPS-M-IN-160 API 599
Valve bonnet and bottom flanges shall be of bolted construction with fully retained gaskets
Trim and seat shall be easily replaceable. seat should be damped or backed up by a seat retainer
Packing material / Packing construction: Teflon/Chevron type
Material test certificate
Dimensional check
Hydrostatic test
Performance and mechanical operation test
Testy certificate including pressure test, visual, Dimensional and nude
Seal leakage test
Casting examination for valves 6 inches and larger in class 600 and higher as per ANSI B 16.34
Casting quality valves shall NDT (RT tested)
Mill test certificate for all metallic parts
6- Screwed bolt-type limit stops, e.g. on the control valve stem, adjustable over the full length of the stroke shall be applied. the vendor shall set the limit/travel stops at the required minimum or maximum valve opening.
7- Environmental Condition For Field Instrumentation Of BINAK oilfield Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: -5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % (Note */ Note**) DB FOR Winter HVAC Design: 6 °C Note * * Refer to " HVAC Design Criteria; N.I.O.C. NO.: F-1-B-422001". ** Refer to “NISOC Meteorological Studies Report".
Relative Humidity:
Maximum Design relative humidity (%): 100Minimum Design relative humidity (%): 0
8- Below content to be considered in process condition for all control valves:
H2S Mol% = W007S ,W035 , W028 , W046S =0.0003 / W018S , W008N = 0.0004
CO2 Mol%= W007S ,W035 , W028 , W046S = 0.0014 / W018S, W008N = 0.0022
CL- Content in formation water is 133504 ppm
MAX. Water CUT: ASMARI =20% , BANGESTAN =60%
9- All Control valves shall be IP 65 and weather proof.
10- Standard ISA75.01 for sizing of Control valves shall be considered by vendor.
11- In accordance to IPS-E-IN-160, Control valve body size normally shall not be less than half of normal line size.
12- 2 Nos. Eye-Bolt and 2 Nos. Jack Bolt for each valve to be supplied by vendor.
13- Quick Change Trim type control valve to be designed by vendor.
14- Main parameters such as Noise level, vibration, actuator sizing, valve construction material, CV factor, Fluid specification, … to be specified as per standard by vendor.
15- The stroking time shall be lower than 5 second for valves up to 4” and 1 second per inch diameter for bigger ones. (VTC)
16- Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. The capacity of the secured instrument air buffer vessel shall be sized for a minimum instrument air supply pressure of 3 barg.

## FCV-1701A
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
| شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | شماره صفحه: 5 از 10
| 9038 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO |  | 110 |  | IN |  | DT |  | 0006 |  |  | D02
Control Valve
GENERAL |  | 1 | Tag No. | [10 empty] | FCV-1701A
|  | 2 | Service | [10 empty] | FROM W018S
|  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CRD-110-171A-FN05-4"-PT | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001 ( 3 of 6 )
|  | 4 | Area Classification | [10 empty] | Zone 2, IIB,T4
|  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | -5 | [7 empty] | 50
|  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH. 80
|  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 4" | [7 empty] | API 5L GR.B, SMLS, BE, ASME, B36.10M
PROCESS CONDITIONS |  | 10 | Fluid | [10 empty] | Crude oil
|  | 11 | State | [10 empty] | mixed / 3phase
|  | 12 | Valve Design Pressure(barg)/ Actuator Shut Off Pressure DP | [10 empty] | 93/93
|  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  | Min.
|  | 14 | Flow Rate(vapor/liquid) | [10 empty] | kg/h |  |  |  |  | 195.88/12285.84 |  |  | 178.076/11168.95 |  | 59.35/3722.98
|  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 12.78 |  |  | 12.78 |  | 12.78
|  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 2
|  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 36.15
|  |  | Molecular Weight(MIX) | [15 empty] | 65.08
|  | 18 | Liquid Specific Gravity (Gl) / Gas Specific Gravity | [15 empty] | 0.909/0.39
|  | 19 | Compressibility Factor(Z)(vapour) | [10 empty] | - |  |  |  |  | 0.9525
|  | 20 | Viscosity (vapour/oil/water) | [10 empty] | cP |  |  |  |  | 0.011/8.89/0.69
|  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.27/1.13
|  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 52.57
|  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 291.2
CALCULATED RESULTS |  | 24 | Flow Coefficient Cv (max-case) | [10 empty] | - |  |  |  |  | BY VENDOR
|  | 25 | Travel (max-case) | [10 empty] | % |  |  |  |  | BY VENDOR
|  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | Max. 85 dBA(VTC) |  |  | Max. 85 dBA(VTC) |  | Max. 85 dBA(VTC)
BODY AND TRIM(Note 6) |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  | Electro-Pneumatic Smart
|  | 28 | Rated Cv |  |  |  | (NOTE 4) | [10 empty] | 51 | Input Signal |  |  |  | 4~20 mA-HART Smart
|  | 29 | End conn. & Rating IN/OUT |  |  |  | 2" # 600 / 2" # 600 (VTC) | [10 empty] | 52 | Power Supply |  |  |  | 24 VDC loop powered
|  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  | ISO M20x 1.5
[18 empty] | 54 | FlowDirection |  |  |  | Flow to Open(VTC)
|  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  | Failure Position/Close
[18 empty] | 56 | Output Signal |  |  |  | 3-15 Psi
|  | 32 | Flow Direction |  |  |  | (NOTE 4) | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  | 65 / EExia |  | Yes
|  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 58 | MFR/Model |  | LCD requirement |  | (NOTE 4) |  | Yes
|  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  | N/A |  | N/A
|  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [10 empty] | 60 | MFR |  | Model |  | N/A |  | N/A
|  | 36 | Guiding |  |  |  | (NOTE 4) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 37 | Rated Travel |  |  |  | (NOTE 4) | [10 empty] | 62 | MFR |  | Model |  | N/A |  | N/A
|  | 38 | Plug/Disk Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  | N/A |  | N/A
|  | 39 | Seat Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  | N/A
|  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  | N/A
|  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  | N/A
|  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 67 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 43 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 68 | MFR |  | Model |  | N/A |  | N/A
ACTUTOR |  | 44 | Size | Eff.Area |  |  | (NOTE 4) |  |  | (NOTE 4) | V.T.A |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  | Yes (NOTE 4)
|  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | TOP MOUNTED | [7 empty] | 70 | Filter |  | Gauge |  | Yes |  | Yes
|  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 71 | Pnumatic Conn. |  |  |  | 1/4 " NPTF
|  | 47 | Actuator Type |  |  |  | spring return and diaphragm type | [10 empty] | 72 | MFR |  | Model |  | (NOTE 4) |  | (NOTE 4)
|  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 | (Note3) |  | 7.5 |  | 8.5 |  | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  | API 598
|  | 49 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 74 | Leakage Class |  |  |  | ANSI IV
[18 empty] | 75 | Performance Test |  |  |  | Required
[14 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  | Required(with Double Ferrule Compression conn.)
[18 empty] | 77 | Tube Material |  |  |  | 316 S.S L
PURCHASE |  | Manufacturer |  |  |  |  | (Note 4) | [10 empty] | 78 | Cable Gland |  |  |  | M20, Nickel plated brass
|  | Model |  |  |  |  | (Note 4) | [10 empty] | 79 | Cable Entry |  |  |  | M20 x 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,"Document No.: BK-SSGRL-PEDCO-110-PI-SP-0001".
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS or any equal hard steel.
D02

## FCV-1701B
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
| شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | شماره صفحه: 6 از 10
| 9038 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO |  | 110 |  | IN |  | DT |  | 0006 |  |  | D02
Control Valve
GENERAL |  | 1 | Tag No. | [10 empty] | FCV-1701B
|  | 2 | Service | [10 empty] | FROM W046S
|  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CRD-110-171B-FN05-4"-PT | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001 ( 3 of 6 )
|  | 4 | Area Classification | [10 empty] | Zone 2, IIB,T4
|  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | -5 | [7 empty] | 50
|  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH. 80
|  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 4" | [7 empty] | API 5L GR.B, SMLS, BE, ASME, B36.10M
PROCESS CONDITIONS |  | 10 | Fluid | [10 empty] | Crude oil
|  | 11 | State | [10 empty] | mixed / 3phase
|  | 12 | Valve Design Pressure(barg)/ Actuator Shut Off Pressure DP | [10 empty] | 93/93
|  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  | Min.
|  | 14 | Flow Rate(vapor/liquid) | [10 empty] | kg/h |  |  |  |  | 712.24/18451.85 |  |  | 647.492/16774.41 |  | 431.66/11182.94
|  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 12.78 |  |  | 12.78 |  | 12.78
|  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 2
|  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 31.37
|  |  | Molecular Weight(MIX) | [15 empty] | 39.09
|  | 18 | Liquid Specific Gravity (Gl) / Gas Specific Gravity | [15 empty] | 0.961/0.40
|  | 19 | Compressibility Factor(Z)(vapour) | [10 empty] | - |  |  |  |  | 0.94
|  | 20 | Viscosity (vapour/oil/water) | [10 empty] | cP |  |  |  |  | 0.011/6.25/0.77
|  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.276/3.66
|  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 96.59
|  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 1140
CALCULATED RESULTS |  | 24 | Flow Coefficient Cv (max-case) | [10 empty] | - |  |  |  |  | BY VENDOR
|  | 25 | Travel (max-case) | [10 empty] | % |  |  |  |  | BY VENDOR
|  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | Max. 85 dBA(VTC) |  |  | Max. 85 dBA(VTC) |  | Max. 85 dBA(VTC)
BODY AND TRIM(Note 6) |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  | Electro-Pneumatic Smart
|  | 28 | Rated Cv |  |  |  | (NOTE 4) | [10 empty] | 51 | Input Signal |  |  |  | 4~20 mA-HART Smart
|  | 29 | End conn. & Rating IN/OUT |  |  |  | 2" # 600 / 2" #600 (VTC) | [10 empty] | 52 | Power Supply |  |  |  | 24 VDC loop powered
|  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  | ISO M20x 1.5
[18 empty] | 54 | FlowDirection |  |  |  | Flow to Open(VTC)
|  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  | Failure Position/Close
[18 empty] | 56 | Output Signal |  |  |  | 3-15 Psi
|  | 32 | Flow Direction |  |  |  | (NOTE 4) | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  | 65 / EExia |  | Yes
|  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 58 | MFR/Model |  | LCD requirement |  | (NOTE 4) |  | Yes
|  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  | N/A |  | N/A
|  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [10 empty] | 60 | MFR |  | Model |  | N/A |  | N/A
|  | 36 | Guiding |  |  |  | (NOTE 4) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 37 | Rated Travel |  |  |  | (NOTE 4) | [10 empty] | 62 | MFR |  | Model |  | N/A |  | N/A
|  | 38 | Plug/Disk Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  | N/A |  | N/A
|  | 39 | Seat Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  | N/A
|  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  | N/A
|  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  | N/A
|  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 67 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 43 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 68 | MFR |  | Model |  | N/A |  | N/A
ACTUTOR |  | 44 | Size | Eff.Area |  |  | (NOTE 4) |  |  | (NOTE 4) | V.T.A |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  | Yes (NOTE 4)
|  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | TOP MOUNTED | [7 empty] | 70 | Filter |  | Gauge |  | Yes |  | Yes
|  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 71 | Pnumatic Conn. |  |  |  | 1/4 " NPTF
|  | 47 | Actuator Type |  |  |  | spring return and diaphragm type | [10 empty] | 72 | MFR |  | Model |  | (NOTE 4) |  | (NOTE 4)
|  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 | (Note3) |  | 7.5 |  | 8.5 |  | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  | API 598
|  | 49 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 74 | Leakage Class |  |  |  | ANSI IV
[18 empty] | 75 | Performance Test |  |  |  | Required
[14 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  | Required(with Double Ferrule Compression conn.)
[18 empty] | 77 | Tube Material |  |  |  | 316 S.S L
PURCHASE |  | Manufacturer |  |  |  |  | (Note 4) | [10 empty] | 78 | Cable Gland |  |  |  | M20, Nickel plated brass
|  | Model |  |  |  |  | (Note 4) | [10 empty] | 79 | Cable Entry |  |  |  | M20 x 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,"Document No.: BK-SSGRL-PEDCO-110-PI-SP-0001".
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS or any equal hard steel.
D02

## FCV-1701C
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
| شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | شماره صفحه: 7 از 10
| 9038 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO |  | 110 |  | IN |  | DT |  | 0006 |  |  | D02
Control Valve
GENERAL |  | 1 | Tag No. | [10 empty] | FCV-1701C
|  | 2 | Service | [10 empty] | FROM W008N
|  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CRD-110-171C-FN05-4"-PT | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001 ( 4 of6 )
|  | 4 | Area Classification | [10 empty] | Zone 2, IIB,T4
|  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | -5 | [7 empty] | 50
|  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH. 80
|  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 4" | [7 empty] | API 5L GR.B, SMLS, BE, ASME, B36.10M
PROCESS CONDITIONS |  | 10 | Fluid | [10 empty] | Crude oil
|  | 11 | State | [10 empty] | mixed / 3phase
|  | 12 | Valve Design Pressure(barg)/ Actuator Shut Off Pressure DP | [10 empty] | 93/93
|  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  | Min.
|  | 14 | Flow Rate(vapor/liquid) | [10 empty] | kg/h |  |  |  |  | 218.94/12262.78 |  |  | 199.04/11147.99 |  | 66.34/3715.99
|  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 12.78 |  |  | 12.78 |  | 12.78
|  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 2
|  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 46
|  |  | Molecular Weight(MIX) | [15 empty] | 77.41
|  | 18 | Liquid Specific Gravity (Gl) / Gas Specific Gravity | [15 empty] | 0.902/0.39
|  | 19 | Compressibility Factor(Z)(vapour) | [10 empty] | - |  |  |  |  | 0.95
|  | 20 | Viscosity (vapour/oil/water) | [10 empty] | cP |  |  |  |  | 0.011/7.60/0.58
|  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.25/1.17
|  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 52.57
|  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 291.2
CALCULATED RESULTS |  | 24 | Flow Coefficient Cv (max-case) | [10 empty] | - |  |  |  |  | BY VENDOR
|  | 25 | Travel (max-case) | [10 empty] | % |  |  |  |  | BY VENDOR
|  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | Max. 85 dBA(VTC) |  |  | Max. 85 dBA(VTC) |  | Max. 85 dBA(VTC)
BODY AND TRIM(Note 6) |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  | Electro-Pneumatic Smart
|  | 28 | Rated Cv |  |  |  | (NOTE 4) | [10 empty] | 51 | Input Signal |  |  |  | 4~20 mA-HART Smart
|  | 29 | End conn. & Rating IN/OUT |  |  |  | 2" # 600 / 2" # 600 (VTC) | [10 empty] | 52 | Power Supply |  |  |  | 24 VDC loop powered
|  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  | ISO M20x 1.5
[18 empty] | 54 | FlowDirection |  |  |  | Flow to Open(VTC)
|  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  | Failure Position/Close
[18 empty] | 56 | Output Signal |  |  |  | 3-15 Psi
|  | 32 | Flow Direction |  |  |  | (NOTE 4) | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  | 65 / EExia |  | Yes
|  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 58 | MFR/Model |  | LCD requirement |  | (NOTE 4) |  | Yes
|  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  | N/A |  | N/A
|  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [10 empty] | 60 | MFR |  | Model |  | N/A |  | N/A
|  | 36 | Guiding |  |  |  | (NOTE 4) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 37 | Rated Travel |  |  |  | (NOTE 4) | [10 empty] | 62 | MFR |  | Model |  | N/A |  | N/A
|  | 38 | Plug/Disk Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  | N/A |  | N/A
|  | 39 | Seat Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  | N/A
|  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  | N/A
|  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  | N/A
|  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 67 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 43 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 68 | MFR |  | Model |  | N/A |  | N/A
ACTUTOR |  | 44 | Size | Eff.Area |  |  | (NOTE 4) |  |  | (NOTE 4) | V.T.A |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  | Yes (NOTE 4)
|  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | TOP MOUNTED | [7 empty] | 70 | Filter |  | Gauge |  | Yes |  | Yes
|  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 71 | Pnumatic Conn. |  |  |  | 1/4 " NPTF
|  | 47 | Actuator Type |  |  |  | spring return and diaphragm type | [10 empty] | 72 | MFR |  | Model |  | (NOTE 4) |  | (NOTE 4)
|  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 | (Note3) |  | 7.5 |  | 8.5 |  | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  | API 598
|  | 49 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 74 | Leakage Class |  |  |  | ANSI IV
[18 empty] | 75 | Performance Test |  |  |  | Required
[14 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  | Required(with Double Ferrule Compression conn.)
[18 empty] | 77 | Tube Material |  |  |  | 316 S.S L
PURCHASE |  | Manufacturer |  |  |  |  | (Note 4) | [10 empty] | 78 | Cable Gland |  |  |  | M20, Nickel plated brass
|  | Model |  |  |  |  | (Note 4) | [10 empty] | 79 | Cable Entry |  |  |  | M20 x 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,"Document No.: BK-SSGRL-PEDCO-110-PI-SP-0001".
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS or any equal hard steel.
D02

## FCV-1701D
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
| شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | شماره صفحه: 8 از 10
| 9038 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO |  | 110 |  | IN |  | DT |  | 0006 |  |  | D02
Control Valve
GENERAL |  | 1 | Tag No. | [10 empty] | FCV-1701D
|  | 2 | Service | [10 empty] | FROM W028
|  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CRD-110-171D-FN05-4"-PT | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001 ( 4 of 6 )
|  | 4 | Area Classification | [10 empty] | Zone 2, IIB,T4
|  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | -5 | [7 empty] | 50
|  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH. 80
|  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 4" | [7 empty] | API 5L GR.B, SMLS, BE, ASME, B36.10M
PROCESS CONDITIONS |  | 10 | Fluid | [10 empty] | Crude oil
|  | 11 | State | [10 empty] | mixed / 3phase
|  | 12 | Valve Design Pressure(barg)/ Actuator Shut Off Pressure DP | [10 empty] | 93/93
|  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  | Min.
|  | 14 | Flow Rate(vapor/liquid) | [10 empty] | kg/h |  |  |  |  | 1316.60/30623.54 |  |  | 1196.917/27839.59 |  | 718.15/16703.75
|  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 12.78 |  |  | 12.78 |  | 12.78
|  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 2
|  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 44.16
|  |  | Molecular Weight(MIX) | [15 empty] | 39.09
|  | 18 | Liquid Specific Gravity (Gl) / Gas Specific Gravity | [15 empty] | 0.953/0.40
|  | 19 | Compressibility Factor(Z)(vapour) | [10 empty] | - |  |  |  |  | 0.9505
|  | 20 | Viscosity (vapour/oil/water) | [10 empty] | cP |  |  |  |  | 0.012/5.39/0.60
|  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.24/1.12
|  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 10.08
|  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 1081
CALCULATED RESULTS |  | 24 | Flow Coefficient Cv (max-case) | [10 empty] | - |  |  |  |  | BY VENDOR
|  | 25 | Travel (max-case) | [10 empty] | % |  |  |  |  | BY VENDOR
|  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | Max. 85 dBA(VTC) |  |  | Max. 85 dBA(VTC) |  | Max. 85 dBA(VTC)
BODY AND TRIM(Note 6) |  | 27 | Body size |  |  |  | 3" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  | Electro-Pneumatic Smart
|  | 28 | Rated Cv |  |  |  | (NOTE 4) | [10 empty] | 51 | Input Signal |  |  |  | 4~20 mA-HART Smart
|  | 29 | End conn. & Rating IN/OUT |  |  |  | 3" # 600 / 3"#600 (VTC) | [10 empty] | 52 | Power Supply |  |  |  | 24 VDC loop powered
|  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  | ISO M20x 1.5
[18 empty] | 54 | FlowDirection |  |  |  | Flow to Open(VTC)
|  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  | Failure Position/Close
[18 empty] | 56 | Output Signal |  |  |  | 3-15 Psi
|  | 32 | Flow Direction |  |  |  | (NOTE 4) | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  | 65 / EExia |  | Yes
|  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 58 | MFR/Model |  | LCD requirement |  | (NOTE 4) |  | Yes
|  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  | N/A |  | N/A
|  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [10 empty] | 60 | MFR |  | Model |  | N/A |  | N/A
|  | 36 | Guiding |  |  |  | (NOTE 4) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 37 | Rated Travel |  |  |  | (NOTE 4) | [10 empty] | 62 | MFR |  | Model |  | N/A |  | N/A
|  | 38 | Plug/Disk Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  | N/A |  | N/A
|  | 39 | Seat Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  | N/A
|  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  | N/A
|  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  | N/A
|  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 67 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 43 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 68 | MFR |  | Model |  | N/A |  | N/A
ACTUTOR |  | 44 | Size | Eff.Area |  |  | (NOTE 4) |  |  | (NOTE 4) | V.T.A |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  | Yes (NOTE 4)
|  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | TOP MOUNTED | [7 empty] | 70 | Filter |  | Gauge |  | Yes |  | Yes
|  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 71 | Pnumatic Conn. |  |  |  | 1/4 " NPTF
|  | 47 | Actuator Type |  |  |  | spring return and diaphragm type | [10 empty] | 72 | MFR |  | Model |  | (NOTE 4) |  | (NOTE 4)
|  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 | (Note3) |  | 7.5 |  | 8.5 |  | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  | API 598
|  | 49 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 74 | Leakage Class |  |  |  | ANSI IV
[18 empty] | 75 | Performance Test |  |  |  | Required
[14 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  | Required(with Double Ferrule Compression conn.)
[18 empty] | 77 | Tube Material |  |  |  | 316 S.S L
PURCHASE |  | Manufacturer |  |  |  |  | (Note 4) | [10 empty] | 78 | Cable Gland |  |  |  | M20, Nickel plated brass
|  | Model |  |  |  |  | (Note 4) | [10 empty] | 79 | Cable Entry |  |  |  | M20 x 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,"Document No.: BK-SSGRL-PEDCO-110-PI-SP-0001".
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS or any equal hard steel.
D02

## FCV-1701E
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
| شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | شماره صفحه: 9 از 10
| 9038 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO |  | 110 |  | IN |  | DT |  | 0006 |  |  | D02
Control Valve
GENERAL |  | 1 | Tag No. | [10 empty] | FCV-1701E
|  | 2 | Service | [10 empty] | FROM W035
|  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CRD-110-171E-FN05-4"-PT | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001 ( 5 of 6 )
|  | 4 | Area Classification | [10 empty] | Zone 2, IIB,T4
|  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | -5 | [7 empty] | 50
|  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH. 80
|  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 4" | [7 empty] | API 5L GR.B, SMLS, BE, ASME, B36.10M
PROCESS CONDITIONS |  | 10 | Fluid | [10 empty] | Crude oil
|  | 11 | State | [10 empty] | mixed / 3phase
|  | 12 | Valve Design Pressure(barg)/ Actuator Shut Off Pressure DP | [10 empty] | 93/93
|  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  | Min.
|  | 14 | Flow Rate(vapor/liquid) | [10 empty] | kg/h |  |  |  |  | 1278.20/30661.96 |  |  | 1162.004/27874.51 |  | 697.2/16724.7
|  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 12.78 |  |  | 12.78 |  | 12.78
|  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 2
|  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 40.47
|  |  | Molecular Weight(MIX) | [15 empty] | 39.09
|  | 18 | Liquid Specific Gravity (Gl) / Gas Specific Gravity | [15 empty] | 0.955/0.40
|  | 19 | Compressibility Factor(Z)(vapour) | [10 empty] | - |  |  |  |  | 0.949
|  | 20 | Viscosity (vapour/oil/water) | [10 empty] | cP |  |  |  |  | 0.012/5.60/0.64
|  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.25/1.12
|  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 96.51
|  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 1140
CALCULATED RESULTS |  | 24 | Flow Coefficient Cv (max-case) | [10 empty] | - |  |  |  |  | BY VENDOR
|  | 25 | Travel (max-case) | [10 empty] | % |  |  |  |  | BY VENDOR
|  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | Max. 85 dBA(VTC) |  |  | Max. 85 dBA(VTC) |  | Max. 85 dBA(VTC)
BODY AND TRIM(Note 6) |  | 27 | Body size |  |  |  | 3" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  | Electro-Pneumatic Smart
|  | 28 | Rated Cv |  |  |  | (NOTE 4) | [10 empty] | 51 | Input Signal |  |  |  | 4~20 mA-HART Smart
|  | 29 | End conn. & Rating IN/OUT |  |  |  | 3" # 600 / 3"#600 ( VTC) | [10 empty] | 52 | Power Supply |  |  |  | 24 VDC loop powered
|  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  | ISO M20x 1.5
[18 empty] | 54 | FlowDirection |  |  |  | Flow to Open(VTC)
|  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  | Failure Position/Close
[18 empty] | 56 | Output Signal |  |  |  | 3-15 Psi
|  | 32 | Flow Direction |  |  |  | (NOTE 4) | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  | 65 / EExia |  | Yes
|  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 58 | MFR/Model |  | LCD requirement |  | (NOTE 4) |  | Yes
|  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  | N/A |  | N/A
|  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [10 empty] | 60 | MFR |  | Model |  | N/A |  | N/A
|  | 36 | Guiding |  |  |  | (NOTE 4) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 37 | Rated Travel |  |  |  | (NOTE 4) | [10 empty] | 62 | MFR |  | Model |  | N/A |  | N/A
|  | 38 | Plug/Disk Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  | N/A |  | N/A
|  | 39 | Seat Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  | N/A
|  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  | N/A
|  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  | N/A
|  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 67 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 43 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 68 | MFR |  | Model |  | N/A |  | N/A
ACTUTOR |  | 44 | Size | Eff.Area |  |  | (NOTE 4) |  |  | (NOTE 4) | V.T.A |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  | Yes (NOTE 4)
|  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | TOP MOUNTED | [7 empty] | 70 | Filter |  | Gauge |  | Yes |  | Yes
|  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 71 | Pnumatic Conn. |  |  |  | 1/4 " NPTF
|  | 47 | Actuator Type |  |  |  | spring return and diaphragm type | [10 empty] | 72 | MFR |  | Model |  | (NOTE 4) |  | (NOTE 4)
|  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 | (Note3) |  | 7.5 |  | 8.5 |  | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  | API 598
|  | 49 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 74 | Leakage Class |  |  |  | ANSI IV
[18 empty] | 75 | Performance Test |  |  |  | Required
[14 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  | Required(with Double Ferrule Compression conn.)
[18 empty] | 77 | Tube Material |  |  |  | 316 S.S L
PURCHASE |  | Manufacturer |  |  |  |  | (Note 4) | [10 empty] | 78 | Cable Gland |  |  |  | M20, Nickel plated brass
|  | Model |  |  |  |  | (Note 4) | [10 empty] | 79 | Cable Entry |  |  |  | M20 x 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,"Document No.: BK-SSGRL-PEDCO-110-PI-SP-0001".
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS or any equal hard steel.
D02

## FCV-1701F
نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR CONTROL/REGULATOR VALVES - EXTENSION OF BINAK B/C MANIFOLD
| شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | شماره صفحه:10 از 10
| 9038 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO |  | 110 |  | IN |  | DT |  | 0006 |  |  | D02
Control Valve
GENERAL |  | 1 | Tag No. | [10 empty] | FCV-1701F
|  | 2 | Service | [10 empty] | FROM W007S
|  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CRD-110-171F-FN05-4"-PT | [7 empty] | BK-W007S-PEDCO-110-PR-PI-0001 ( 5 of 6)
|  | 4 | Area Classification | [10 empty] | Zone 2, IIB,T4
|  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | -5 | [7 empty] | 50
|  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH. 80
|  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 4" | [7 empty] | API 5L GR.B, SMLS, BE, ASME, B36.10M
PROCESS CONDITIONS |  | 10 | Fluid | [10 empty] | Crude oil
|  | 11 | State | [10 empty] | mixed / 3phase
|  | 12 | Valve Design Pressure(barg)/ Actuator Shut Off Pressure DP | [10 empty] | 93/93
|  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  | Min.
|  | 14 | Flow Rate(vapor/liquid) | [10 empty] | kg/h |  |  |  |  | 515.64/12260.413 |  |  | 468.769/11145.83 |  | 5572.91/5572.91
|  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 12.78 |  |  | 12.78 |  | 12.78
|  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 2
|  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 41.52
|  |  | Molecular Weight(MIX) | [15 empty] | 39.09
|  | 18 | Liquid Specific Gravity (Gl) / Gas Specific Gravity | [15 empty] | 0.954/0.40
|  | 19 | Compressibility Factor(Z)(vapour) | [10 empty] | - |  |  |  |  | 0.9501
|  | 20 | Viscosity (vapour/oil/water) | [10 empty] | cP |  |  |  |  | 0.012/5.54/0.63
|  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.25/1.12
|  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 96.59
|  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 1140
CALCULATED RESULTS |  | 24 | Flow Coefficient Cv (max-case) | [10 empty] | - |  |  |  |  | BY VENDOR
|  | 25 | Travel (max-case) | [10 empty] | % |  |  |  |  | BY VENDOR
|  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | Max. 85 dBA(VTC) |  |  | Max. 85 dBA(VTC) |  | Max. 85 dBA(VTC)
BODY AND TRIM(Note 6) |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER (Note 5) |  |  |  | 50 | Type |  |  |  | Electro-Pneumatic Smart
|  | 28 | Rated Cv |  |  |  | (NOTE 4) | [10 empty] | 51 | Input Signal |  |  |  | 4~20 mA-HART Smart
|  | 29 | End conn. & Rating IN/OUT |  |  |  | 2" # 600 / 2" # 600 (VTC) | [10 empty] | 52 | Power Supply |  |  |  | 24 VDC loop powered
|  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  | ISO M20x 1.5
[18 empty] | 54 | FlowDirection |  |  |  | Flow to Open(VTC)
|  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  | Failure Position/Close
[18 empty] | 56 | Output Signal |  |  |  | 3-15 Psi
|  | 32 | Flow Direction |  |  |  | (NOTE 4) | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  | 65 / EExia |  | Yes
|  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 58 | MFR/Model |  | LCD requirement |  | (NOTE 4) |  | Yes
|  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  | N/A |  | N/A
|  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [10 empty] | 60 | MFR |  | Model |  | N/A |  | N/A
|  | 36 | Guiding |  |  |  | (NOTE 4) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 37 | Rated Travel |  |  |  | (NOTE 4) | [10 empty] | 62 | MFR |  | Model |  | N/A |  | N/A
|  | 38 | Plug/Disk Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  | N/A |  | N/A
|  | 39 | Seat Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  | N/A
|  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  | N/A
|  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  | N/A
|  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 67 | I.P. |  | Ex.Protec. |  | N/A |  | N/A
|  | 43 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 68 | MFR |  | Model |  | N/A |  | N/A
ACTUATOR |  | 44 | Size | Eff.Area |  |  | (NOTE 4) |  |  | (NOTE 4) | V.T.A |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  | Yes (NOTE 4)
|  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | TOP MOUNTED | [7 empty] | 70 | Filter |  | Gauge |  | Yes |  | Yes
|  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 71 | Pnumatic Conn. |  |  |  | 1/4 " NPTF
|  | 47 | Actuator Type |  |  |  | spring return and diaphragm type | [10 empty] | 72 | MFR |  | Model |  | (NOTE 4) |  | (NOTE 4)
|  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 | (Note3) |  | 7.5 |  | 8.5 |  | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  | API 598
|  | 49 | MFR | Model |  |  | (NOTE 4) |  |  |  | (NOTE 4) | [6 empty] | 74 | Leakage Class |  |  |  | ANSI IV
[18 empty] | 75 | Performance Test |  |  |  | Required
[14 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  | Required(with Double Ferrule Compression conn.)
[18 empty] | 77 | Tube Material |  |  |  | 316 S.S L
PURCHASE |  | Manufacturer |  |  |  |  | (Note 4) | [10 empty] | 78 | Cable Gland |  |  |  | M20, Nickel plated brass
|  | Model |  |  |  |  | (Note 4) | [10 empty] | 79 | Cable Entry |  |  |  | M20 x 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,"Document No.: BK-SSGRL-PEDCO-110-PI-SP-0001".
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.
5- Bypass line and isolating valve shall be considered for valve positioner by vendor.
6- Trim part material shall be considered as minimum 316SS or any equal hard steel.
D02