## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-BK15-PEDCO-110-SU-DW-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0962 |  |  | Transmital Date: 16-May-2022
Document Title: Over Head Line Plan and Profile - BK15 |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-SU-TR-0962 |  |  | Transmital Date: 16-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-BK15-PEDCO-110-SU-DW-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اينكه در مدرك محاسبات كشش-فلش سيم اسپن هاي مورد بررسي از 50 تا 150 ميباشد، ولي شاهد استفاده از اسپن هاي بيشتر از بازه مذكور در مدرك ارسالي هستيم كه اين موضوع ميبايست در مدرك محاسبات خط از حيث حداكثر فلش و حداكثر اسپن امكان پذير، بررسي گردد و در صورت نياز مدارك پيش نياز به روز رساني گردد. |  | BK-SUR-ENG-ELE-01-04476 | 2022-05-29 | مطابق با مسیر پیشنهادی، طول مسیر خط افزایش یافت و بر هیمن اساس، این مدرک مورد ویرایش قرار گرفته است.
2 | See attached file for more comments. |  | BK-SUR-ENG-ELE-01-04476 | 2022-05-29
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-2022 |  |  |  |  | Date: