| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CALCULATION REPORT FOR EXTENSION OF EXISTING ELECT. BUILDING نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| D00 | SEP. 2022 | IFC | R.Berlouie | M.Fakharian | M.Mehrshad |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class:2 |  | CLIENT Doc. Number:F0Z-709120 |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X |  |  |  |  |  | 66 |  |  |  |  |  |
| 2 | X |  |  |  |  |  | 67 |  |  |  |  |  |
| 3 | X |  |  |  |  |  | 68 |  |  |  |  |  |
| 4 | X |  |  |  |  |  | 69 |  |  |  |  |  |
| 5 | X |  |  |  |  |  | 70 |  |  |  |  |  |
| 6 | X |  |  |  |  |  | 71 |  |  |  |  |  |
| 7 | X |  |  |  |  |  | 72 |  |  |  |  |  |
| 8 | X |  |  |  |  |  | 73 |  |  |  |  |  |
| 9 | X |  |  |  |  |  | 74 |  |  |  |  |  |
| 10 | X |  |  |  |  |  | 75 |  |  |  |  |  |
| 11 | X |  |  |  |  |  | 76 |  |  |  |  |  |
| 12 | X |  |  |  |  |  | 77 |  |  |  |  |  |
| 13 | X |  |  |  |  |  | 78 |  |  |  |  |  |
| 14 | X |  |  |  |  |  | 79 |  |  |  |  |  |
| 15 | X |  |  |  |  |  | 80 |  |  |  |  |  |
| 16 | X |  |  |  |  |  | 81 |  |  |  |  |  |
| 17 | X |  |  |  |  |  | 82 |  |  |  |  |  |
| 18 | X |  |  |  |  |  | 83 |  |  |  |  |  |
| 19 | X |  |  |  |  |  | 84 |  |  |  |  |  |
| 20 | X |  |  |  |  |  | 85 |  |  |  |  |  |
| 21 | X |  |  |  |  |  | 86 |  |  |  |  |  |
| 22 | X |  |  |  |  |  | 87 |  |  |  |  |  |
| 23 | X |  |  |  |  |  | 88 |  |  |  |  |  |
| 24 | X |  |  |  |  |  | 89 |  |  |  |  |  |
| 25 | X |  |  |  |  |  | 90 |  |  |  |  |  |
| 26 | X |  |  |  |  |  | 91 |  |  |  |  |  |
| 27 | X |  |  |  |  |  | 92 |  |  |  |  |  |
| 28 | X |  |  |  |  |  | 93 |  |  |  |  |  |
| 29 | X |  |  |  |  |  | 94 |  |  |  |  |  |
| 30 | X |  |  |  |  |  | 95 |  |  |  |  |  |
| 31 | X |  |  |  |  |  | 96 |  |  |  |  |  |
| 32 | X |  |  |  |  |  | 97 |  |  |  |  |  |
| 33 | X |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 | X |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 | X |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 | X |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 | X |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 | X |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 | X |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 | X |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 | X |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 | X |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 | X |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 | X |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 | X |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 | X |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 | X |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 | X |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 | X |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 | X |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 | X |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 | X |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 | X |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 | X |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 | X |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 | X |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 | X |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 | X |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 | X |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 | X |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 | X |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 | X |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 | X |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 | X |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 | X |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	Scope	5

3.0	NORMATIVE REFERENCES	5

3.1	Local Codes and Standards	5

3.2	International Codes and Standards	5

3.3	The Project Documents	5

3.4	ENVIRONMENTAL DATA	5

3.5	Order of Precedence	5

4.0	DESIGN INFORMATION	6

4.1	Structure LOCATION	6

4.2	ARCHITECTURAL PLANS	7

5.0	material properties	9

5.1	reinforced concrete	9

5.2	cement	9

5.3	STIFFNESS MODIFICATION	10

6.0	design loads	10

6.1	general	10

6.2	DEAD LOAD	12

6.3	LIVE LOAD	14

6.4	Snow LOAD	14

6.5	wind LOAD	15

6.6	HORIZONTAL SEISMIC LOAD	17

6.7	Redundancy Factor ρ	21

6.8	BLAST LOAD	21

7.0	Structural design	24

7.1	LOAD COMBINATIONS FOR REINFORCED CONCRETE STRUCTURE	25

7.2	capacitor bank design	35

7.3	CO2 ROOM design	50

7.4	transformer ROOM design	58

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

As a part of the Project, a New Gas Compressor Station (adjacent to existing Binak GCS) shall be constructed to gather of 15 MMSCFD (approx.) associated gases and compress & tra	nsfer them to Siahmakan GIS.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – Surface Fcilities; New Gas Compressor Station |
| EPD/EPC CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection (D&I) Companies |
| VENDOR: | The firm or person who will fabricate the equipment or material. |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | The firm appointed by EPD/EPC CONTRACTOR (GC) and approved by CLIENT (in writing) for the inspection of goods. |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- Scope

This document covers minimum necessary requirements for the design, selection, manufacture and inspection.

- NORMATIVE REFERENCES

## Local Codes and Standards

- IPS-E-PR-905                  	Engineering Standard for Process Design of Dryers

- IPS-E-PR-330	Engineering Standard for Process Design of Compressed Air Systems

## International Codes and Standards

- ASTM	American Society for Testing Materials Relevant Parts

- API 610	Centrifugal Pumps for General Refinery Service, 10th Edition

- ISO 15156	Petroleum and Natural Gas Industries. Materials for use in H2S Containing Environments in Oil and Gas Production

## The Project Documents

- --------------------------	Process Basis of Design

- --------------------------	Process Design Criteria

## ENVIRONMENTAL DATA

Refer to "Process Basis of Design; Doc. No. -----------------------".

## Order of Precedence

In case of any conflict between the contents of this document or any discrepancy between this document and other project documents or reference standards, this issue must be reported to the CLIENT. The final decision in this situation will be made by CLIENT.

- DESIGN INFORMATION

## Structure LOCATION

The Capacitor bank and Co2 Room and Transformers room  is located in Binak oilfield.

Figure 1- Project Location

## ARCHITECTURAL PLANS

Figure 2 – CAPACITOR BANK AND CO2 ROOM

Figure 3 – SECTION A-A

Figure 4 – TRANSFORMER ROOM PLAN

Figure 5 – SECTION A-A

- material properties

## reinforced concrete

Concrete shall generally conform to the specification for concrete work report No:BK-GNRAL-PEDCO-000-ST-SP-001- The following properties of concrete are used.

Lean concrete: f’c =150 kg/cm2

Cast in place concrete: f’c =350 kg/cm2

Where f'c is the minimum compressive characteristic strength of a cylinder specimen at 28 days.

Young Modulus of concrete: Ec=15100f'c  kg/cm2

Poisson's Ratio: ν = 0.2

Unit weight of reinforced concrete: 2500 kg/m3

## cement

Cement shall conform to the following specifications for Portland cement:

a) "Standard Specification for Portland Cement" (ASTM C 150). [5.1, 6.1.1]

Cement type shall be considered according to geotechnical investigation report.

Cement used in the work shall correspond to that on which selection of concrete proportions was based. [5.1, 6.1.2]

Fly Ash or other pozzolans shall conform to  ASTM  C  618   "Standard Specification for Coal Fly Ash and Raw or Calcined Natural Pozzolan for Use in Concrete" For more information about other kinds of pozzolans see Iranian national concrete code Publication No.-120 of management and planning organization part 3-6- 4-2. [5.1, 6.1.3]

## STIFFNESS MODIFICATION

For analysis of concrete structure, the following modifications for flexural stiffness of elements are considered.

Columns………………………………..0.7Ig

Beams………………………………….0.35Ig

Wall (Cracked)……………..………….0.35Ig

Slabs………………………….……….0.25Ig

- design loads

## general

Considered loads are as follows.

- Dead Loads.

- Live Loads.

- Snow Load.

- Wind Load.

- Earthquake Load.

- Blast load.

- Thermal Load

Table 1- Define Load Patterns

| Define Load Patterns |  |  |  |  |
| --- | --- | --- | --- | --- |
| Load Pattern Name | Type | CAPACITOR BANK | CO2 ROOM | TRANSFORMER ROOM |
| DEAD | Dead |  |  |  |
| Wall | Dead |  |  |  |
| Live | Live |  |  |  |
| Wind | Wind |  |  |  |
| EX | Quake |  |  |  |
| EY | Quake |  |  |  |
| EV | Quake |  |  |  |
| BLAST1 | Live |  |  |  |
| BLAST2 | Live |  |  |  |
| BLAST3 | Live |  |  |  |
| BLAST4 | Live |  |  |  |
| Th+20 | Temperature |  |  |  |
| Th-20 | Temperature |  |  |  |

## DEAD LOAD

Dead Load is considered as the weight of materials forming a permanent part of the structure plant. The weight of materials of construction incorporated into the building, including but not limited to walls, floors, roofs, ceilings, stairways, built-in partitions, finishes, cladding and other similarly incorporated architectural and structural items, and the weight of fixed service equipment, such as plumbing stacks and risers, electrical feeders, heating, ventilating and air-conditioning systems.

Specific weight of materials which will be used is based on Iranian National Building Code, Part 6, where applicable. Other weights are in accordance with the specifications and/or drawings of vendors and manufacturers.

Here is the calculation of design dead load for floors, walls including External and Internal walls.

Table 2- Calculation of Roof Dead load (for Capacitor bank and Co2 Room)

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | ceramic | 2400 | 2.0 | 48 |
| 2 | cement mortar | 2100 | 2.0 | 42 |
| 3 | 2 layer bitumen & gunny | ------ | ------- | 15.0 |
| 4 | cement mortar | 2100 | 2.5 | 52.5 |
| 5 | Expanded aggregate | 850 | 10 | 85 |
| 6 | Slab 20 cm | Calculated by Sap | ----- | ----- |
| 7 | Thermal insulation of polystyrene | 100 | 10 | 10 |
| 8 | Plaster and soil mortar | 1600 | 2 | 32 |
| 9 | Gypsum Plaster | 1300 | 1 | 13 |
|  | SUM |  |  | 297.5 |
|  | Applied to model |  |  | 300 |

Table 3- Calculation of Roof Dead load (for Transformers Room)

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | 0.9MM GALVANIZED METAL SHEET | 7850 | 0.09 | 7 |
| 2 | Z PURLIN(18) | - | - | 8 |
| 7 | Thermal insulation of polystyrene | 100 | 10 | 10 |
| 9 | Roof installation plate | 1300 | 1 | 10 |
|  | SUM |  |  | 35.0 |
|  | Applied to model |  |  | 50 |

Table 4- Calculation of external Wall Dead load

| NO. | Description | specific weight (kg/m3) | thickness (cm) | kg/m2 |
| --- | --- | --- | --- | --- |
| 1 | FACADE FINE BRICK | 2100 | 20 | 420 |
|  |  | SUM |  | 420 |
|  |  | Applied to model |  | 420 |

## LIVE LOAD

Live Load is defined as the weight of all movable loads, including partition walls, personnel, tools, miscellaneous equipment and temporarily stored materials.

Generally where applicable, the live loads shall be in accordance with Iranian National Building Code, Part 6. The Live Loads is generally considered as uniformly distributed over the horizontal projection of the loaded areas, except for the loads with a concentrated nature.

The live load has been considered according to the following table.

Table 5- Live load on structure.

| NO. | Level | kg/m2 |
| --- | --- | --- |
| 1 | Roof (for Capacitor bank and Co2 Room) | 150 |
| 2 | Roof (for Transformers Room) | 50 |

For the ceiling of the transformer room, the point load of 1000 kg in the most critical point taken into account separately.

## Snow LOAD

The snow load according to the sixth topic of the national building regulations is as follows.

Pr=Is.Cn.Ch.Cs.Ps

Is=1.2

Cn=0.8

Ch=1.2

Cs:

α=10° < α0=15→Cs=1

Ps=According to table 6-7-1 and paragraph 6-7-3, it is equal to  0.25 KN/m2

→Pr=1.2*0.8*1.2*1*0.25=0.29KNm2<Roof live load=0.5KNm2

⇒The roof live load is selected for design.

## wind LOAD

The wind load according to the sixth topic of the national building regulations is as follows.

Considering that the transformer building is covered from the north side by the electrical room and its doors are covered by a metal grid, the main wind directions on the transformer building include the external wind perpendicular to the roof slope and the internal wind blowing in the direction of the roof slope.

- EXTERNAL WIND LOAD

P=Iw.q.Ce.Ct.Cg .Cp.Cd

Iw=1.2

q=According to table 6-10-1, it is equal to 0.68KNm2

Ce=Z100.2≥0.9=0.9

Z=6.0m

Ct=1

Cd=0.85

Table 6- Combined coefficients CpCg

| Slope roof | The body of the building |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0° to 90° | 1 | 1E | 2 | 2E | 3 | 3E | 4 | 4E | 5 | 5E | 6 | 6E |
|  | -0.85 | -0.9 | -1.3 | -2 | -0.7 | -1 | -0.85 | -0.9 | 0.75 | 1.15 | -0.55 | -0.8 |

Table 7-External wind pressure perpendicular to the roof slope

| Slope roof | External wind pressure perpendicular to the roof slope (KN/m^2) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0° to 90° | 1 | 1E | 2 | 2E | 3 | 3E | 4 | 4E | 5 | 5E | 6 | 6E |
|  | -0.55 | -0.56 | -0.81 | -1.25 | -0.45 | -0.65 | -0.55 | -0.56 | 0.5 | 0.75 | -0.35 | -0.5 |

- INTERNAL WIND LOAD

Pi=Iw.q.Ce.Ct.Cgi .Cpi.Cd

Iw=1.2

q=According to table 6-10-1, it is equal to 0.68KNm2

Ce=Z100.2≥0.9=0.9

Z=6.0m

Ct=1

Cgi=2

Cpi=-0.7 to 0.7

Cd=0.85

Pi=-0.9KNm2 to  0.9 KNm2

## HORIZONTAL SEISMIC LOAD

According to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition) the structure shall be designed for earthquake load in two orthogonal directions.

Base level is defined as the level below which the structure does not move relative to the ground during an earthquake. For this structure base level is top of the deck level.

Basic parameters which are used in calculation of earthquake forces are presented below.

Following formula is used for calculations according to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition)

Vu=SaRuIW

In which:

Vu: Basic shear

Sa: mapped spectral response acceleration parameter (𝑔)

I: Importance factor of structure

Ru: Structural system factor

W= effective seismic weight of the structure, including dead loads and other loads, calculated from base level.

Table 8- Basic parameters used for earthquake loads calculation

(CAPACITOR BANK BUILDING)

| Height of the structure from the base level (m) | 5.30 |
| --- | --- |
| Importance factor, I | 1.5 |
| Structural system | Special reinforced concrete shear walls |
| Soil type | II |
| A | 0.30 |
| Ru | 5 |
| Ct | 0.05 |
| x | 0.75 |
| Tx&Y (calculation) =Ct.Hx | 0.174 |
| Tx (analysis) – mode 2 | 0.289 |
| Ty (analysis) – mode1 | 0.49 |
| Tx&Y (select for design) =1.4 Tcalculation | 0.24 |
| B=B1*N & N=1 | 2.5 |
| Sax & Say | 0.75 |
| Kx & Ky →T<0.5 | 1 |
| Cmin=0.044SDSI | 0.165 |
| Cx& Cy=SaxRuI | 0.22 |
| Cx*ρ & Cy*ρ-(ρ=1.3) | 0.286 |
| Service level earthquake =1/6.A.B.I | 0.187<0.286-O.K |

Table 9- Basic parameters used for earthquake loads calculation

(CO2 ROOM)

| Height of the structure from the base level (m) | 5.30 |
| --- | --- |
| Importance factor, I | 1.5 |
| Structural system | Sway Special |
| Soil type | II |
| A | 0.30 |
| Ru | 8 |
| Ct | 0.047 |
| x | 0.9 |
| Tx&Y (calculation) =Ct.Hx | 0.21 |
| Tx (analysis) – mode 2 | 0.854 |
| Ty (analysis) – mode1 | 0.885 |
| Tx&Y (select for design) =1.4 Tcalculation | 0.294 |
| B=B1*N & N=1 | 2.5 |
| Sax & Say | 0.75 |
| Kx & Ky →T<0.5 | 1 |
| Cmin=0.044SDSI | 0.165 |
| Cx& Cy=SaxRuI | 0.14 |
| Cx*ρ & Cy*ρ -(ρ=1.3) | 0.182 |
| Cx for drift control | 0.088 |
| Cy for drift control | 0.085 |
| Service level earthquake =1/6.A.B.I | 0.187≈0.182→O.K |

Table 10- Basic parameters used for earthquake loads calculation

(TRANSFORMERS ROOM)

| Height of the structure from the base level (m) | 4.90 |
| --- | --- |
| Importance factor, I | 1.5 |
| Structural system | Non-building Structure |
| Soil type | II |
| A | 0.30 |
| Ru | 3 |
| Tx (analysis) – mode 3 | 0.14 |
| Ty (analysis) – mode22 | 0.014 |
| Bx=B1x*N & N=1 | 2.5 |
| By=B1y*N & N=1 | 1.21 |
| Sax | 0.75 |
| Say | 0.36 |
| Kx & Ky →T<0.5 | 1 |
| Cmin=0.044SDSI | 0.165 |
| Cx=SaxRuI | 0.375 |
| Cy=SayRuI | 0.18 |
| Cx*ρ -(ρ=1.3) | 0.487 |
| Cy*ρ -(ρ=1) | 0.18 |

## Redundancy Factor ρ

According to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition Paragraph 4-6) - ρ =1.3

## BLAST LOAD

According to Appendix IC of IPS-E-CE-500 (ADDITIONAL REQUIREMENTS FOR BLAST RESISTANT BUILDINGS AND STRUCTURES), the blast pressure of exterior walls and roof are as below:

Table 11- Blast Load

| Item | Pr | P0 | t0 |
| --- | --- | --- | --- |
|  | Kpa | Kpa | msec |
| Front Wall | 172 |  | 20 |
| Back Wall |  | 70 | 20 |
| Right Wall | 172 |  | 20 |
| Left Wall | 172 |  | 20 |
| Roof |  | 70 | 20 |

Figure 6- Mode 1 in Blast Load

Figure 7- Mode 2 in Blast Load

Figure 8- Mode 3 in Blast Load

Figure 9- Mode 4 in Blast Load

- Structural design

## dynamic increase factor

- fdy=SIF*DIF*fy

- fdu=SIF*DIF*fu

- f'dc=SIF*DIF*f'c

Table 12- dynamic increase factor

| Material | Concrete |  | Rebar |  | St37 |  | St52 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | SIF | DIF | SIF | DIF | SIF | DIF | SIF | DIF |
| fdy | - | - | 1.15 | 1.20 | 1.15 | 1.25 | 1.15 | 1.2 |
| fdu | - | - | 1.15 | 1.05 | 1.15 | 1.1 | 1.15 | 1.05 |
| f'dc | 1.1 | 1.15 | - | - | - | - | - | - |

## LOAD COMBINATIONS FOR REINFORCED CONCRETE STRUCTURE

These load combinations will be considered according to the Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition Design)

Table 13- Load combination for design (Capacitor bank-earth quake)

Table 14- Load combination for design (Capacitor bank-Blast load)

Table 15- Load combination for design (Capacitor bank and Transformer room -Thermal load)

Table 16- Load combination for Soil control- (Capacitor bank)

Table 17- Load combination for design (transformer room)

Table 18- Load combination for design (Co2 room)

Table 19- Load combination for Soil control (Co2 Room)

Table 20- Load combination for Soil control (Co2 room)

Figure 10- 3D MODEL OF CAPACITOR BANK

Figure 11- 3D MODEL OF CO2 ROOM

Figure 12- 3D MODEL OF TRANSFORMER ROOM

## capacitor bank design

## Wall design (capacitor bank)

| (MAX M11+) BLAST1 | (MAX M11+) BLAST 2 |
| --- | --- |
| (MAX M11+) BLAST3 | (MAX M11+) BLAST 4 |

Figure 13- MAX M11+ (ton-m)

| (MAX M11-) BLAST1 | (MAX M11-) BLAST 2 |
| --- | --- |
| (MAX M11-) BLAST3 | (MAX M11-) BLAST 4 |

Figure 14- MAX M11-(ton-m)

| (MAX M22+) BLAST1 | (MAX M22+) BLAST 2 |
| --- | --- |
| (MAX M22+) BLAST3 | (MAX M22+) BLAST 4 |

Figure 15- MAX M22+(ton-m)

| (MAX M22-) BLAST1 | (MAX M22-) BLAST 2 |
| --- | --- |
| (MAX M22-) BLAST3 | (MAX M22-) BLAST 4 |

Figure 16- MAX M22-(ton-m)

| (MAX V) BLAST1 | (MAX V) BLAST 2 |
| --- | --- |
| (MAX V) BLAST3 | (MAX V) BLAST 4 |

Figure 17- MAX V(ton)

Table 21- WALL RESULTANT FORCES (CAPACITOR BANK)

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Blast load | 11.0 | 14.0 | 13.7 | 16.0 | 20.0 |
| Earth Quake | 0.9 | 0.5 | 1.3 | 1.4 | 3.17 |
| Thermal | 7.2 | 7.5 | 6.30 | 6.35 | 15 |
| Select for design | 11.0 | 14.0 | 13.70 | 16.0 | 20.0 |

Table 22- WALL DESIGN (CAPACITOR BANK)

Table 23- WALL DESIGN (CAPACITOR BANK)

Table 24- WALL ROTATION ANGLE (CAPACITOR BANK)

| WALL ROTATION ANGLE-(UFC 3-340) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Wall | Load | Xm (cm) | H (cm) | θ°max | Control |
| Wall “a” | Blast-1 | 1.2 | 530 | 0.25 | O.K |
| Wall “b” | Blast-2 | 0.98 | 530 | 0.21 | O.K |
| Wall “c” | Blast-3 | 0.30 | 530 | 0.032 | O.K |
| Wall ”d” | Blast-4 | 0.48 | 530 | 0.10 | O.K |

Vu=20.0 ton

Vn=Vc+Vs

Vc=f'c6bwd=44.261000*240=265932.32N=26.59 ton

Vu>0.5Vc=13.295

USE∅8@300x300mm

Vs=Av.fy.ds=50.24*552*240300=22185.98*3=66557.95 N=6.65 ton

Vn=26.59+6.65=33.24 ton.>20 ton. →O.K

## slab design(capacitor bank)

| MAX M11(+) | MAX M11(-) |
| --- | --- |
| MAX M22(+) | MAX M22(-) |

Figure 18- MAX SLAB RESULTANT FORCES

Table 25- SLAB RESULTANT FORCES (CAPACITOR BANK)

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Blast load | 7.0 | 5.5 | 4.5 | 8.0 | 14.0 |
| Earth Quake | 0.5 | 1.25 | 0.92 | 1.40 | 2.25 |
| Thermal | 0.43 | 1.26 | 0.92 | 1.37 | 2.04 |
| Select for design | 7.0 | 5.5 | 4.5 | 8.0 | 14.0 |

Table 26- SLAB DESIGN (CAPACITOR BANK)

Table 27- SLAB DESIGN (CAPACITOR BANK)

Table 28- SLAB ROTATION ANGLE (CAPACITOR BANK)

| WALL ROTATION ANGLE-(UFC 3-340) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| SLAB | Load | Xm (cm) | H (cm) | θ°max | Control |
| ROOF | Blast | 1.6 | 420 | 0.43 | O.K |

Vu=14.0 ton

Vn=Vc+Vs

Vc=f'c6bwd=44.261000*150=166207.7N=16.62 ton

Vu>0.5Vc=8.31

USE∅8@300x300mm

Vs=Av.fy.ds=50.24*552*150300=13866.24*3=41598.72 N=4.15 ton

Vn=16.62+4.15=20.77 ton.>14.0 ton. →O.K

## settlement of the foundation  (capacitor bank)

Table 29- FOUNDATION DISPLACEMENTS-EARTH QUAKE LOAD-cm (CAPACITOR BANK)

Table 30- FOUNDATION DISPLACEMENTS- BLAST LOAD -cm (CAPACITOR BANK)

The maximum settlement of the foundation =3.5 cm <5cm – O.K

## slipe control (capacitor bank)

Table 31- BASE REACTION –EARTH QUAKE LOAD –(CAPACITOR BANK)

Table 32- BASE REACTION –BLAST LOAD –(CAPACITOR BANK)

Fs=TfT=Tp+(N'tan∅+cL)T

Tp=Kp.γ.h2*0.5*L*2=2.66*1.8*1.52*0.5*9.10*2=98.0ton

∅=27°

Kp=1+sin∅1-sin∅=2.66

N'=sum dead load=240.0+20.0=260.0ton

c=0

T=177.0-48.0=129 ton~130 ton

Fs=98+260*tan27130=1.77>1.5 IPS→O.K

## Foundation design for resultant forces (capaciotr bank)

Table 33- FOUNDATION RESULTANT FORCES-EARTH QUAKE LOAD (CAPACITOR BANK)

Table 34- FOUNDATION RESULTANT FORCES-BLAST LOAD (CAPACITOR BANK)

Table 35- FOUNDATION DESIGN (CAPACITOR BANK)

Vu=50.0 ton

Vn=Vc+Vs

Vc=f'c6bwd=44.261000*525=581726.95N=58.17 ton

Vu>0.5Vc=29.08ton

USE∅8@200x200mm

Vs=Av.fy.ds=50.24*552*525200=72797.76*5=363988.8 N=36.39 ton

Vn=58.17+36.39=94.56 ton.>50.0 ton. →O.K

## DRIFT CONTROL (capaciotr bank)

The design lateral displacement (nonlinear) at level 𝑥 shall be calculated from Equation below according to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition).

δx=CdδxeI

𝛿𝑥𝑒= elastic lateral displacement at level 𝑥, according to lateral load distribution from Equivalent Lateral Load Procedure or Modal Response Spectrum Analysis.

Stiffness modification for drift calculation:

Flat slabs & plates = 0.25 Ig

Beams = 0.35 Ig

Columns =0.7 Ig

Wall =0.35 Ig

Table 36- Drift Control (cm)

∆ex&∆ey≪0.011.5=0.0066→O.K

## CO2 ROOM design

## COLUMN design (co2 room)

Figure 19- Column P-M-M Interaction Ratios

## beam design (co2 room)

Figure 20- Beam Design (Longitudinal Reinforcement)

Figure 21- Beam Design (Torsion Reinforcing)

## slab design (co2 room)

| MAX M11 | MAX M22 |
| --- | --- |
| MAX V13 | MAX V23 |

Figure 22- MAX SLAB RESULTANT FORCES-(tom-m)

Table 37- SLAB RESULTANT FORCES (CO2 ROOM)

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| ENVELOPE | 2.0 | 2.8 | 1 | 2.5 | 5 |

Table 38- SLAB DESIGN (CO2 ROOM)

Vu=5 ton

Vn=Vc+Vs

Vc=f'c6bwd=3561000*150=147901.9N=14.7 ton

Vu<0.5Vc=7.35→O.K

## settlement of the foundation (co2 room)

Table 39- FOUNDATION DISPLACEMENTS -cm (CO2 ROOM)

The maximum settlement of the foundation =2.5 cm <5cm – O.K

## Foundation design for resultant forces (co2 Room)

| MAX M11 | MAX M22 |
| --- | --- |
| MAX V13 | MAX V23 |

Figure 23- MAX FOUNDATION RESULTANT FORCES-ENVELOPE COMBO-(ton-m)

Table 40- FOUNDATION RESULTANT FORCES (CO2 ROOM)

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| ENVELOPE | 6 | 10 | 3 | 8 | 20 |

Table 41- FOUNDATION DESIGN (CO2 ROOM)

Vu=10 ton

Vn=Vc+Vs

Vc=f'c6bwd=3561000*425=419055.65N=41.90 ton

Vu<0.5Vc=20.95→O.K

## DRIFT CONTROL (CO2 Room)

The design lateral displacement (nonlinear) at level 𝑥 shall be calculated from Equation below according to Iranian Seismic Design Code for Petroleum Facilities (Pub.038-16-3rd edition).

δx=CdδxeI

𝛿𝑥𝑒= elastic lateral displacement at level 𝑥, according to lateral load distribution from Equivalent Lateral Load Procedure or Modal Response Spectrum Analysis.

Stiffness modification for drift calculation:

Flat slabs & plates = 0.25 Ig

Beams = 0.35 Ig

Columns =0.7 Ig

Wall =0.35 Ig

Table 42- Drift Control (cm)

∆ex&∆ey<0.0151.5=0.01→O.K

## transformer ROOM design

## WALL design (transformer room)

| MAX M11(+) | MAX M11(-) |
| --- | --- |
| MAX M22(+) | MAX M22(-) |

Figure 24- MAX WALL RESULTANT FORCES-ENVELOPE COMBO-(ton-m)

Table 43- WALL RESULTANT FORCES (Transformer room)

| RESULTANT FORCES |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| LOAD | M11(ton-m) |  | M22(ton-m) |  | V (ton) |
|  | MAX (+) | MAX (-) | MAX (+) | MAX (-) | MAX |
| Envelope | 1.7 | 1.7 | 5.6 | 5.2 | 3.65 |

Table 44- WALL DESIGN (TRANSFORMER ROOM)

Table 45- WALL DESIGN (TRANSFORMER ROOM)

Vu=3.65 ton

Vn=Vc+Vs

Vc=f'c6bwd=3561000*200=197202.65N=19.72 ton

Vu=3.65 ton<0.5Vc=9.86 ton→O.K

## PURLIN design (transformer room)

Figure 25- PURLIN DESIGN –UNP 120

## PURLIN Deformed control (transformer room)

Table 46- LOAD COMBINATION FOR PURLIN DEFORMED CONTROL (TRANSFORMER ROOM)

Table 47- PURLIN DEFORMATION CONTROL (TRANSFORMER ROOM)

| Def<L/240 | L/240 | Length(cm) | Deformation(cm) | Load combination |
| --- | --- | --- | --- | --- |
| O.K | 1.77 | 425 | 1.0 | Deflection 2 |

## FOUNDATION design (transformer room)

The characteristic of the soil under the foundation according to the geotechnical report no. BK-GCS-PEDCO-120-GT-RT-0001 is as follows.

Table 48- SUBSTRATE REACTION MODULUS

| (kg/cm3) Substrate reaction modulus |  |  |  | B(m) |
| --- | --- | --- | --- | --- |
| L/B=10 | L/B=5 | L/B=2 | L/B=1 |  |
| 1.09 | 1.14 | 1.33 | 1.69 | 1.0 |
| 0.77 | 0.78 | 0.85 | 1.00 | 2.0 |
| 0.64 | 0.65 | 0.69 | 0.78 | 3.0 |
| 0.57 | 0.57 | 0.60 | 0.68 | 4.0 |
| 0.53 | 0.53 | 0.55 | 0.61 | 5.0 |

Table 49- LOAD COMBINATION FOR SOIL CONTROL. (TRANSFORMER ROOM)

Figure 26- DEFORMED SHAPE

The maximum deformation of the foundation is 0.5 cm, the deformation shown is much less than 5 cm.

Figure 27- SOIL STRESS UNDER THE FOUNDATION

The maximum soil stress under the foundation is 0.8 kg/cm^2.

Figure 28- X DIRECTION REINFORCEMENT DESIGN

Use Ø16@20cm +Ø16Add.

Figure 29- Y DIRECTION REINFORCEMENT DESIGN

Use Ø16@20cm +Ø16Add.