## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-HV-PY-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0978 |  |  | Transmital Date: 14/MAY/2022
Document Title: Plumbing & Sewage Piping Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-HV-TR-0978 |  |  | Transmital Date: 14/MAY/2022
[5 empty] | CRS No: NISOC-CRS-BK-GNRAL-PEDCO-220-HV-PY-0001-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت بررسی مدرک فوق لازم است مدرک محاسبات مربوط به اندازه گیری لوله های آب و فاضلاب برای این امور ارسال گردد. |  | 00/2294/111558 | 1400/03/31 | با توجه به اینکه مدرک محاسبات در MDL برای این مورد تعریف نشده در خود نقشه جدول مقادیر FIXTURE UNIT و سرعت آب برای آب مصرفی و همچنین جدول مقادیر FIXTURE UNIT و شیب مجاز لوله های فاضلاب در خط لوله اصلی و سرشاخه های فرعی محاسبه و مشخص شده است.
2 | لوله های پلی پروپیلن3اینچ با 90میلی متر معادل می باشد. |  | 00/2294/111558 | 1400/03/31 | سایز های اصلی لوله های فاضلاب با اتصالات پوش فیت 50،75،110 میلی متر هستند و سایز 90 توسط سازنده های داخلی تولید نمی‌شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: H.ADINEH | Signature
| Date: |  |  |  |  | Date: 03/SEP/2022