## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-HV-PY-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0978 |  |  | Transmital Date: 14/MAY/2022
Document Title: Plumbing & Sewage Piping Layout |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-HV-TR-0978 |  |  | Transmital Date: 14/MAY/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-220-HV-PY-0001-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | to add regulation valve after first pressure gauge and before inlet of water to building for valve box (this is for protection of exceed pressure above 4 bar) |  | BK-SUR-ENG-HVC-01-04924 | 2022-06-29 | Its not applicable. Because network pressure is under 4bar.
2 | to add condensate drain piping on this drawing-it is preffered to drain water discharged to green spaces (condensate pit inside of green space) |  | BK-SUR-ENG-HVC-01-04924 | 2022-06-29 | due to high numbers of split units and their distances, this is impossible to drain water discharged to green spaces. spilt drainage discharge to areas around building.
3 | since size of PEX-AL-PEX pipes (ISIRI 12753) in IMPERIAL and METRIC (regarding to inside diameter in camparison with steel pipe ASTM A53 ) are as follow 3/8" 17.1mm 16mm 1/2" 21.3mm 20mm 3/4" 26.7mm 25mm 1" 33.4mm 32mm ............... all sizes shall modify accordingly -for review and check |  | BK-SUR-ENG-HVC-01-04924 | 2022-06-29 | it has done according to vendors technical document and their tables for sizing of 5 layers piping.
4 | same as item 3, PP pipe size (based on EN 1451) shall modify based on actual inside diameter (in camparison with steel pipe ASTM A53 )-for review and check |  | BK-SUR-ENG-HVC-01-04924 | 2022-06-29 | it has done according to vendors available sizes.
5
6
7
8
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 06/29/2022 |  |  |  |  | Date: 03/SEP/2022