## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR PRESSURE GAUGE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | W007S | PEDCO | 110 |  | IN | DT | 0002 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR PRESSURE GAUGE - EXTENSION OF BINAK B/C MANIFOLD نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | SEP.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAR.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | DEC.2021 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-707972
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved
D02

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR PRESSURE GAUGE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | W007S |  | PEDCO | 110 | IN | DT | 0002 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR PRESSURE GAUGE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  | BK | W007S | PEDCO | 110 | IN | DT |  | 0002 | D02
REFERENCE DOCUMENTS :
| Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
| Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| P&ID - Extension of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-PR-PI-0001
| Piping Material Specification | [6 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
| Instrument & Control System Design Criteria | [6 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
| Process Flow Diagram - Extension of Binak B/C Manifold | [6 empty] | BK-W007S-PEDCO-110-PR-PF-0001

## Notes
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR PRESSURE GAUGE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0002 | D02
GENERAL NOTES:
1- Pressure elements shall be capable of withstanding intermittent over-ranging to 1.3 times the maximum scale reading.
2- Ranges shall be selected suitable to have the operating pressure in the middle third of the scale.
3- Vendor to follow materials indicated in the Data Sheets, related wetted parts, these materials can be as minimum and shall be verified by vendor.
4- Gauges shall be supplied with syphon on steam services which operating temperatures are more than 100⁰C.
5- Tag plate shall be stainless steel. Following details shall be engraved on them:
• Tag Number • Range limit • Service • Manufacturer model and serial number
6- Weep hole shall be provided on the case bottom of all gauges.
7- Material Test Certificate and Calibration Certificate for all gauges to be submitted by vendor.
8- Each pressure gauge which doesn’t have Diaphragm Seal shall be supplied with a Two (Process Conn. 1/2"NPTF, 316 S.S.). Manifold to be supplied by vendor
9- Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C) Minimum ambient temperature: -5 (°C) Maximum steel surface exposed to sun: 85 (°C) Maximum summer dry bulb: - (°C) DB/RH for Summer HVAC Design: 41 °C / 61 % (Note */ Note**) DB FOR Winter HVAC Design: 6 °C Note * * Refer to " HVAC Design Criteria; N.I.O.C. NO.: F-1-B-422001". ** Refer to “NISOC Meteorological Studies Report".
Relative Humidity:
• Maximum Design relative humidity (%): 100 • Minimum Design relative humidity (%): 0
D02

## PG
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بستههای کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR PRESSURE GAUGE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK | W007S | PEDCO | 110 | IN | DT | 0002 | D02
PRESSURE GAUGE
| GENERAL | 1 | Tag No. |  | P&ID No. |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6
|  | 2 | Service |  | Piping Class |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6
|  | 3 | Area Clacification |  |  |  |  | Zone 2, IIB T4
| PROCESS CONDITION | 4 | Fluid |  | Phase |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6
|  | 5 | Operating. Pressure |  | Design. Pressure |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6 |  | (barg)
|  | 6 | Operating. Temperature |  | Design. Temperature |  |  | SEE PAGE 6 | [5 empty] | SEE PAGE 6 |  | (°C)
|  | 7 | Min. Design Metal Temperature |  |  |  |  | SEE PAGE 6 | [7 empty] | (°C)
|  | 8 | Range |  |  |  |  | SEE PAGE 6
| GAUGE | 9 | Type |  |  |  |  | Pressure Gauge-Direct Reading
|  | 10 | Instrument Range |  |  |  |  | SEE PAGE 6
|  | 11 | Liquid Filled |  |  |  |  | Silicon - SEE PAGE 6~9 |  |  |  | (Note 5 in Below Table)
|  | 12 | Mounting |  |  |  |  | Local
|  | 13 | Dial Size |  | Dial Color | Zero Adjustment |  | 150 mm | (Note 3 in Below Table) |  |  |  |  | White with black lettering | Adjustable pointer
|  | 14 | Case Material |  |  |  |  | 304 SS |  |  |  | (Note 2 in Below Table)
|  | 15 | Blow-Out Protection |  |  |  |  | Required-Back
|  | 16 | Lens Material |  |  |  |  | Shatter proof glass
|  | 17 | Pressure Element Type |  |  |  |  | SEE PAGE 6
|  | 18 | Pressure Element Material |  |  |  |  | SEE PAGE 6
|  | 19 | Connection Material |  |  |  |  | 316 S.S
|  | 20 | Connection Size |  |  |  |  | 1/2 " NPT
|  | 21 | Connection Location |  |  |  |  | Bottom
|  | 22 | Movement Material |  |  |  |  | 316 S.S
|  | 23 | Nominal Accuracy |  |  |  |  | 0.6% of full scale
|  | 24 | Weather Protection |  |  |  |  | IP-65 as minimum
| DIAPHRAGM SEAL | 25 | Type |  |  |  |  | N/A
|  | 26 | Size (In) |  |  |  |  | N/A
|  | 27 | Diaphragm Material |  |  |  |  | N/A
|  | 28 | Fill Fluid |  |  |  |  | N/A
|  | 29 | Capillary Length |  |  |  |  | N/A
|  | 30 | Capillary Material |  |  |  |  | N/A
31
| OPTIONS | 32 | Movement Damping |  |  |  |  | SEE PAGE 6
|  | 33 | Overrange Protection |  |  |  |  | SEE PAGE 6 (1.3 of F.S) (Note 7 in Below Table)
|  | 34 | Siphon |  | Material |  |  | SEE PAGE 6 | [6 empty] | 316L S.S
|  | 35 | Manifold |  | Body Material |  |  | 2 Way Manifold | [6 empty] | 316L S.S
|  | 36 | Process Connection |  | Rating |  |  | SEE PAGE 6 (Note 6 in Below Table) | [6 empty] | SEE PAGE 6
|  | 37 | Manifold Model |  | Manifold Manufacturer |  |  | Will be finalized later |  |  |  |  | Will be finalized later
|  | 38 | NACE Requirements |  |  |  |  | SEE PAGE 6 |  |  |  |  | (Note 1 in Below Table )
|  | 39 | Solid front |  |  |  |  | Yes
40
| PURCHASING DATA | 41 | Model No. |  | Manufacturer |  |  | Will be finalized later |  |  |  |  | Will be finalized later
|  | 42 | Supplier |  | Order |  |  | Will be finalized later |  |  |  |  | Will be finalized later
43
44
| NOTES : | VTA : Vendor to Advise
(1) NACE-MR-0175/ISO 15156 requirements shall be covered where Piping/Pipeline Material Specification recommended.
(2) Window shall be heavy plate glass, breakage resistance and shatter proof.
(3) Pressure gauges shall be double scale type (Bar and Psi).
(4) All gauges shall be equipped with screw driver slot type adjustment for calibration purposes.
(5) All gauges near pumps and compressors that have vibration shall be equipped with adjustable restriction snubber.
(6) 1/2"NPT for Instrument/Process connection and 1/4" NPT for Drain Connection-All Manifolds, Pulsation Dampners and Siphons shall be suitable for connecting to gauges.
(7) Over range protection shall be 1.3 times the maximum range.
(8) Vendor is responsible for applying suitable accessories to prevent damage and to reach required accuracy for PG.
D02
D02
D02

## PG LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني، تسهیلات برق‌رسانی مربوط به موقعیت W007S و توسعه چندراهه کلاستر بینک
DATA SHEETS FOR PRESSURE GAUGE - EXTENSION OF BINAK B/C MANIFOLD
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  |  | BK |  | W007S |  | PEDCO |  | 110 | IN |  | DT |  | 0002 |  | D02
PRESSURE GAUGE
Rev. | Item No. | Tag No. | P&IDs No. | Service. | LINE/ EQUIPMENT | Piping Class | Schedule | Connection Rating | Process Connection | Fluid | Phase | Operating Pressure (barg) | Design Pressure (barg) | Operating Temperature (°C) | Design Temperature(°C) | Range (barg) | Liquid. Filled | Press. Element Type | Press. Element Material | Movement Damping | Over Range Protection | Snubber | Siphon | Diaphragm Seal | Nace | Model | Remark
D02 MODIFIED | 1 | PG-1701A | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W018S | CRD-110-111-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 36.31/22.62 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 2 | PG-1702A | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W018S | CRD-110-111-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 36.31/22.62 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 3 | PG-1703A | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W018S | CRD-110-171A-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 93 | 36.31/22.62 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 4 | PG-1704A | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W018S | CRD-110-179A-CN05-4"-PT | CN05 | SCH.40 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 10.78 | 41.5 | 36.15/22.49 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 5 | PG-1701B | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W046S | CRD-110-131B-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 31.60/15.20 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 6 | PG-1702B | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W046S | CRD-110-131B-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 31.60/15.20 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 7 | PG-1703B | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W046S | CRD-110-171B-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 93 | 31.60/15.20 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 8 | PG-1704B | BK-W007S-PEDCO-110-PR-PI-0001 (3/6) | from W046S | CRD-110-179B-CN05-4"-PT | CN05 | SCH.40 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 10.78 | 41.5 | 31.37/15.00 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 9 | PG-1701C | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W008N | CRD-110-161-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 46.19/33.90 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 10 | PG-1702C | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W008N | CRD-110-161-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 46.19/33.90 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 11 | PG-1703C | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W008N | CRD-110-171C-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 93 | 46.19/33.90 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 12 | PG-1704C | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W008N | CRD-110-179C-CN05-4"-PT | CN05 | SCH.40 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 10.78 | 41.5 | 46.00/33.75 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 13 | PG-1701D | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W028 | CRD-110-141-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 44.41/32.15 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 14 | PG-1702D | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W028 | CRD-110-141-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 44.41/32.15 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 15 | PG-1703D | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W028 | CRD-110-179D-CN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 93 | 44.41/32.15 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 16 | PG-1704D | BK-W007S-PEDCO-110-PR-PI-0001 (4/6) | from W028 | CRD-110-171D-CN05-4"-PT | CN05 | SCH.40 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 10.78 | 41.5 | 44.16/31.92 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 17 | PG-1701E | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W035 | CRD-110-151-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 40.71/27.31 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 18 | PG-1702E | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W035 | CRD-110-151-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 40.71/27.31 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 19 | PG-1703E | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W035 | CRD-110-171E-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 93 | 40.71/27.31 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 20 | PG-1704E | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W035 | CRD-110-179E-CN05-4"-PT | CN05 | SCH.40 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 10.78 | 41.5 | 40.47/27.09 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 21 | PG-1701F | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W007S | CRD-110-121-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 41.77/22.21 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 22 | PG-1702F | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W007S | CRD-110-121-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 207 | 41.77/22.21 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 23 | PG-1703F | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W007S | CRD-110-171F-FN05-4"-PT | FN05 | SCH.80 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 12.78 | 93 | 41.77/22.21 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 24 | PG-1704F | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | from W007S | CRD-110-171F-CN05-4"-PT | CN05 | SCH.40 | 6000# Notes 6,8 in Previous Page | 1/2" NPT | CRUDE OIL | 2PHASE (LIQUID/VAPOR) | 10.78 | 41.5 | 41.52/22.00 | 85 | 0-25 | Yes | Bourdon | SS 316L | No | Yes | No | No | No | Yes | VTA | Note 1 in Previous Page
D01 MODIFIED | DELETED | PG-1701 | BK-W007S-PEDCO-110-PR-PI-0001 (5/6) | OIL SUMP | CDH-110-171G-AN05-3"-PT | AN05 | SCH.40 | 3000# Notes 6,8 in Previous Page | 1/2" NPT | LIQUID | 1PHASE (LIQUID) | ATM | 3.5 | AMB | 85 | 0-6 | Yes | Bourdon | SS 316L | No | No | No | No | No | Yes | VTA | Note 1 in Previous Page
D02 MODIFIED | 25 | PG-1702 | BK-W007S-PEDCO-110-PR-PI-0001 (6/6) | OIL SUMP | CDH-110-171G-CN05-3"-PT | CN05 | SCH.40 | 3000# Notes 6,8 in Previous Page | 1/2" NPT | 1PHASE (LIQUID) | 1PHASE (LIQUID) | 11.5 | 14.1 | AMB | 85 | 0-25 | Yes | Bourdon | SS 316L | No | No | No | No | No | Yes | VTA | Note 1 in Previous Page
D02