## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W046S-PEDCO-110-PR-PI-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0653 |  |  | Transmital Date: 23.Feb.2022
Document Title: P&ID - W0046S |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-0653 |  |  | Transmital Date: 23.Feb.2022
[5 empty] | CRS No: NISOC-CRS-BK-W046S-PEDCO-110-PR-PI-0001_D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بعد از stone trap و قبل از کاهنده خط جریانی چاه‌ها فشار سنج در نظر گرفته شود. |  | 01/2294/43153 | 1401/02/08 | نقشه‌های P&ID فوق بر اساس نقشه‌ی طراحی پایه و شماتیک استاندارد به شماره‌ی S5L9002_001A تهیه گردیده‌اند. در صورتی که از منظر آن کارفرمای محترم اضافه نمودن تجهیز فوق الزام آور می‌باشد خواهشمند است مراتب را امر به ابلاغ فرمایند.
2 | به منظور تسهیل در استقرار دستگاه تفکیک‌گر، سه عدد انشعاب 2" کلاس 3000 با شیر دروازه‌ای، در محل بعد از شیر سوخت، بعد از تله سنگ و بعد از شیر بهره‌برداری مورد نیاز می‌باشد. |  | 01/2294/43153 | 1401/02/08 | نقشه‌های P&ID فوق بر اساس نقشه‌ی طراحی پایه و شماتیک استاندارد به شماره‌ی S5L9002_001A تهیه گردیده‌اند. در صورتی که از منظر آن کارفرمای محترم اضافه نمودن تجهیز فوق الزام آور می‌باشد خواهشمند است مراتب را امر به ابلاغ فرمایند.
3 | مشخصات خط لوله قبل و بعد از شیر بهره‌برداری باید یکسان در نظر گرفته شود. در مدارک ارسالی مشخصات خط لوله از LN15 به LN12 تغییر داده شود. |  | 01/2294/43153 | 1401/02/08 | مشخصات بر اساس آخرین PMS اصلاح گردید.
4 | شایان ذکر است که در مدارک S&L صرفا در خصوص عدد چهارم توضیح کلی داده شده است و لازم است که مقادیر C.A ذکر گردد. |  | 01/2294/43153 | 1401/02/08 | به مدرک PMS رجوع شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021