## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-BK15-PEDCO-110-AR-DW-0002 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0974 |  |  | Transmital Date: 18/05/2022
Document Title: Architectural Drawing For Switchgear Building of Well Pads - BK15 |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-AR-T-0974 |  |  | Transmital Date:18/05/2022
[5 empty] | CRS No: NISOC-CRS-BK-BK15-PEDCO-110-AR-DW-0002_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مقتضی است یک اتاق با کاربری انبار در ساختمان کلیدخانه جانمایی گردد. پیشنهاد می‌شود، اتاق باطری به مقدار ۹۰ درجه چرخیده و اتاق ترانس نیز به منتهی الیه ساختمان شیفت داده شود. اتاق مذکور در فضای ایجاد شده بین اتاق باتری و اتاق ترانس با عرض تقریبا ۳ متر و طول ۳.۵ متر جانمایی گردد. |  | 1401-2294-85268 | 1401/03/10 | احتراما مطابق جلسات مهندسی ارزش، کاربری مورد نیاز مورد بحث قرار گرفت و فضاهای مورد نیاز برای سوییچ گیر، اتاق باتری و شلتر ترانسفورماتور براساس خروجی آن جلسات می باشد
2 | ترانشه روبروی درب کوچک کلیدخانه بصورت مسقف بتنی و یا بصورت کاندوییت بانک اجرا شود. |  | 1401-2294-85268 | 1401/03/10 | انجام شد.
3 | چیدمان الکتریکی نمایش داده شده، در این مدرک می‌باسیت بر اساس مدرک چیدمان تجهیزات الکتریکی BK-SSGRL-PEDCO-110-EL-PY-0008 اصلاح گردد. |  | 1401-2294-85268 | 1401/03/10 | انجام شد.
4 | ضروری است مطابق استاندارد IPS-E-EL-100 بند ۷.۶.۷.۳ دریچه‌ای در قسمت پایین اتاق باتری مطابق با شماتیک موجود در بند ذکر شده استاندارد جهت FORCED CLEAN AIR در نظر گرفته شود. |  | 1401-2294-85268 | 1401/03/10 | با توجه به اقلیم منطقه و احتمال ورودی خاک به درون فضا و کاهش عمر باتری‌ها، تهویه هوا به‌وسیله اگزاست و مطابق استاندارد ذکر شده انجام خواهد شد.
5 | یک سپتیک جداگانه برای اتاق باتری در نظر گرفته شود. |  | 1401-2294-85268 | 1401/03/10 | انجام شد
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: