## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0003-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0737 |  |  | Transmital Date: 26-Mar-2022
Document Title: DC Charger Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0737 |  |  | Transmital Date: 26-Mar-2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-SL-0003-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پس از نهایی شدن سایزینگ شارژر و باتری های مربوط به آن مقادیر ظرفیت تجهیزات می بایست در مدرک اعمال گردد. |  | 1401-2294-31452 | 1401-01-30 | مدرک محاسباتی UPS بر اساس بارهای اعلامی بخش ابزاردقیق ویرایش شده است. همچنین فیدرهای این مدرک مطابق با فیدرهای لیست بار ابزادرقیق می باشد. در صورت هرگونه نغییر در مدرک محاسباتی، این مدرک بازنگری خواهد شد.
2 | پیرو بازدید انجام شده از واحد کلاستر بینک، در صورتی که مقرر گردید، جهت شارژر فایرآلارم و باتری های آن از پیشنهاد سازندگان استفاده شود، این مدرک می بایست بر این اساس اصلاح شود. |  | 1401-2294-31452 | 1401-01-30 | پیرو بازدید به عمل آمده مورخ 1401/06/08 از کلاستر بینک، اتاق سیستم 24 VDC در محل ساختمان موجود در نظر گرفته شد. بر این اساس شارژرهای سیستم F&G محاسبه گردیده است. در صورت نیاز از پیشنهادات سازندگان استفاده خواهد شد.
4 | ولتاژ ورودی سیستم 380/400/440 با تلرانس %10± تعریف گردد. |  | 1401-2294-31452 | 1401-01-30 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Mar-22 |  |  |  |  | Date: