## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0003-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0737 |  |  | Transmital Date: 26-Mar-2022
Document Title: DC Charger Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0737 |  |  | Transmital Date: 26-Mar-2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-EL-SL-0003-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on DC charger calculation. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | مدرک محاسباتی DC Charger بر اساس بارهای اعلامی بخش ابزاردقیق ویرایش شده است. همچنین فیدرهای این مدرک مطابق با فیدرهای لیست بار ابزادرقیق می باشد. در صورت هرگونه نغییر در مدرک محاسباتی، این مدرک بازنگری خواهد شد.
2 | This documents shall be revised after site visit and NISOC confirmation, in terms of whether the DC UPS is industrial or commercial. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | پیرو بازدید به عمل آمده مورخ 1401/06/08 از کلاستر بینک، اتاق سیستم 24 VDC در محل ساختمان موجود در نظر گرفته شد. بر این اساس شارژرهای سیستم F&G محاسبه گردیده است. در صورت نیاز از پیشنهادات سازندگان استفاده خواهد شد.
3 | Symbol of MCCB shall be modified on all pages (shall be considered thermal/magnet adjustable). Meanwhile the symbol of MCB on page 6 shall be modified. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Mar-22 |  |  |  |  | Date: