## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0020_D04 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1375 |  |  | Transmital Date: 07/Sep/2022
Document Title: Mechanical Data Sheets For Glycol Transfer Pumps |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0106-ME-TR-1375 |  |  | Transmital Date: 07/Sep/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-ME-DT-0020_D04 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | As per the previous comment which has noted, a note mentioned that the hydrotest shall not be less than 24 barg; this comment can be closed if you confirm that this item will be calrified in TCL. |  | BK-SUR-ENG-MEC-01-05690 | 2020-09-13 | Noted, MAWP and hydrotest pressure will be finalized at vendor's offer stage and TCL. In addition reference standard for this pump is ISO 5199 that shall be followed by vendor.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature |  |  |  | Clarified By: H. Adineh | Signature | M. Fakharian
| Date: |  |  |  |  | Date: 11/23/2022