## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-DG-0001-D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1141 |  |  | Transmital Date: 05-Jul-2022
Document Title: Electrical Typical Schematic Diagrams For LV Panels of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0104-EL-TR-1141 |  |  | Transmital Date: 05-Jul-2022
[5 empty] | CRS No: NISOK-CRS-BK-SSGRL-PEDCO-110-EL-DG-0001-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | در فیدر موتوری بر روی درب تابلو ، جهت قطع مدار یکعدد پوش Stop Stay put کفایت می کند ، پوش دوم Stop حذف شود. |  | 1401-2294-183489 | 1401-05-27 | اعمال گردید.
2 | در فیدر موتوری ، پوش Stop اضطراری در ابتدای مسیر قبل از کنتاکت OL منتقل شود. |  | 1401-2294-183489 | 1401-05-27 | اعمال گردید.
3 | محل تغذیه بخش حفاظت ولتاژی رله MPR ، قبل از کنتاکتور و بعد از سوئیچ فیوز نمایش داده شود. |  | 1401-2294-183489 | 1401-05-27 | اعمال گردید.
4 | کنتاکت مربوط به VOLTAGE OK INCOMING A فقط در مسیر سرویس قرار داشته باشد. |  | 1401-2294-183489 | 1401-05-27 | اعمال گردید.
5 | پوش باتن STOP در مسیر بوبین MX به صورت STAY PUT نمایش داده شود. |  | 1401-2294-183489 | 1401-05-27 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 17-Jul-22 |  |  |  |  | Date: