## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-DG-0001-D03 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1141 |  |  | Transmital Date: 05-Jul-2022
Document Title: Electrical Typical Schematic Diagrams For LV Panels of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0104-EL-TR-1141 |  |  | Transmital Date: 05-Jul-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-DG-0001-D03 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | "LV Switchgear Single Line Diagram " shall be issued before this document and this document shall be revised after finalizing or minor comments on "LV Switchgear single Line Diagram". (Consideration shall be given, according to basic single line diagram, some typical circuit diagram is not applicable for well pads) |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | مطابق با تک خطی تیپیکال های اضافی حذف گردید. |  |  | Noted and Closed.
2 | Technical characteristics and related protection for diesel generator has not been shown. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
3 | Pages 17&20: According to electrical system design criteria, each motor starter/feeder will have a 400/230 V isolating transformer for control circuits, so it shall be deleted from pages 17&20 and shall be shown on outgoing feeders. (Consideration shall be given control voltage for incoming feeders will be supplied by DC UPS) |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | برای تمامی فیدرهای مربوط به هر باسبار ترانس ایزوله 400/230 در نظر گرفته می شود. به صورت یک نوت اضافه گردید. |  |  | Noted and Closed.
4 | Protection shall be modified and considered base on IPS-E-EL-100(1), section 7.5.4.3. (For example 50N,51N, 63P shall be added.) |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
5 | It shall be clarify why some protection has been considered built in ACB circuit breaker (Ig> and Ig>>), While has been considered integrated protection unit. For this size of panel (630A) built in protection functions in the circuit breaker can be enough |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | تمامی حفاظت های مد نظر در داخل کلید دیده می شود. |  |  | Noted and Closed.
6 | Pages 17&20: Considered separated lockout relay for ACB shall be deleted. Meanwhile lock out relay shall be connected to circuit breaker. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
7 | Pages 17&20: According to basic single line diagram, there is not any bus tie for LV switchgear of Well Pads, so the bus tie or coupler word shall be deleted on pages 17&20. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
8 | Motor outgoing feeders shall be protected by on load switch disconnecting fuse not fuse. Meanwhile, all switch disconnecting fuse shall be equipped with a striker pin so that their operation causes the contactor to disconnect. In addition, an independent signal light should be considered for its operation on the starter door. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
9 | Use a three-winding PT instead of three two-winding PT for incoming feeders. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | با توجه به BUILT-IN بودن کلید ورودی حفاظت های ولتاژی درون آن قرار دارد، از این رو ترانس ولتاژ مورد نیاز به صورت دو سیم پیچه می باشد که یا به صورت تک هسته ای یا سه هسته ای خواهد بود. |  |  | Noted and Closed.
10 | Note1 for ammeter on pages 7&8 and 10&11 shall be added and specified. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | Note1 حذف گردید. |  |  | Noted and Closed.
11 | Over load relay rating above 72 ampere shall be C.T. operated. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
12 | Emergency stop pushbutton shall be considered for all incoming and outgoing feeders on switchgear front. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | به صورت یک نوت اضافه گردید. |  |  | Noted and Closed.
13 | Technical characteristics of Corbalance CT on pages 8&11, PT for incomings feeders, etc. shall be added and specified. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
14 | Description of symbols shall be rechecked and modified. (For example description of ACB on pages 4 is similar to MCCB) |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | توضیحات مربوط به هر سیمبل بازنگری گردید. |  |  | Noted and Closed.
15 | All symbols shall be added and specified on symbol pages. |  | BK-SSR-ENG-ELE-00-01506 | 2021-09-13 | اعمال گردید. |  |  | Noted and Closed.
16 | According to our telephone conversation, mechanical transformer protections (63,71,26) shall be connected to Seperat lock out relay (Flagged and Locked Send&Receive Relay ) in LV switchgear. |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | اعمال گردید. |  |  | Noted and Closed.
17 | As per NISOC Comment CB in the DGCP shall be normal open and ACB in the MCC shall be considered Normal Close |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | اعمال گردید. |  |  | Noted and Closed.
18 | It shall be clarify why MPR has been mentioned on page 10, While has been considered seperat protections for motor feeder type M3. |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | پیرو صحبت های انجام شده MPR در نظر گرفته نشد. |  |  | Noted and Closed.
19 | There is no control system in well pads to monitoring, so the considered transducer for incoming feeders can be deleted. |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | اعمال گردید. |  |  | Noted and Closed.
20 | In the schematice type F3 and F6, Trip circuit need to recheck deu to 50Gf and MCCB trip Normal close contact are series instead of parallel. |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | دلیل سری بودن کنتاکتها NO FAULT می باشد که به صورت NC نمایش داده شده است و با توجه به به اینکه کنتاکت NC رله شیشه ای سر راه چراغ سیگنال می باشد ، در صورت بروز خطا چراغ سیگنال روشن می شود. |  |  | Noted and Closed.
21 | in the schematice type F3 and F6, please clarify about "S" normal open contact befor shunt trip |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | حرف اضافه حذف گردید. |  |  | Noted and Closed.
22 | In Schematic type "M2,M3" remote start command shall be modified to "ST DCS". |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | اعمال گردید |  |  | Noted and Closed.
23 | In Schematic type "M2,M3" motor stop status signal shall be considered to sending to the DCS in case of required. |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | سیگنال و فرمان های مورد نیاز به صورت زیر است: Local/Remote Status Running Status Fault Status Start Command Stop Command Trip Command |  |  | Noted and Closed.
24 | In Schematic type "M3" trip contacts "OL", "50G", "47" shall be connected in parallel. |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | دلیل سری بودن کنتاکتها NO FAULT می باشد که به صورت NC نمایش داده شده است و با توجه به به اینکه کنتاکت NC رله شیشه ای سر راه چراغ سیگنال می باشد ، در صورت بروز خطا چراغ سیگنال روشن می شود. |  |  | Noted and Closed.
25 | Schematic diagrams for main and emergency incoming shall be modified based of project requirements. Issued schematic diagram is not as per required logic and need to generally revised |  | BK-SUR-ENG-ELE-01-04072 | 2022-04-26 | با توجه به نیاز پروژه، نقشه اسکماتیک مورد بازبینی قرار گرفت. |  |  | Noted and Closed.
26 | No Comment. NOTE: Some items hall be rechecked and Deleted/Modified in the Manufacturer drawings such as seperat voltage protection on page 11, signals lamps, IRP, etc. |  | BK-SUR-ENG-ELE-01-04487 | 2022-05-30 | بعد از انجام قرارداد و مشخص شدن سازنده، موارد باقی مانده در جلسات شفاف سازی با وندور نهایی خواهد شد. و در مدرک لحاظ می گردد. |  |  | Noted and Closed.
25 | No Comment. Note 1: this document shall be modified based on comments on SLD. For example there is confilict between this document and SLD in the voltage sample connection point at both incoming feeders. Note 2: control logic diagram "BK-SSGRL-PEDCO-110-EL-LD-0001_D02" shall be mentioned as reference document. |  | BK-SUR-ENG-ELE-01-05158 | 2022-07-17 | مغایرات بین این مدرک و دیاگرام تک خطی مرتفع گردید. همچنین مدرک لاجیک به عنوان مرجع اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 17-Jul-22 |  |  |  |  | Date: