## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0737 |  |  | Transmital Date: 26-Mar-2022
Document Title: UPS Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0737 |  |  | Transmital Date: 26-Mar-2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-EL-SL-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پس از نهایی شدن سایزینگ UPS و باتری های مربوط به آن مقادیر ظرفیت تجهیزات می بایست در مدرک اعمال گردد. |  | 1401-2294-31452 | 1401-01-30 | مدرک محاسباتی UPS بر اساس بارهای اعلامی بخش ابزاردقیق ویرایش شده است. همچنین فیدرهای این مدرک مطابق با فیدرهای لیست بار ابزادرقیق می باشد. در صورت هرگونه نغییر در مدرک محاسباتی، این مدرک بازنگری خواهد شد.
2 | پس از مشخص شدن سایز کابل ورودی، در نقشه SLD کابل تغذیه ورودی به صورت 4 رشته لحاظ گردد. |  | 1401-2294-31452 | 1401-01-30 | سایز کابل چهار رشته در نظر گرفته شد.
3 | بار های سیستم UPS به همراه خروجی های یدکی در تابلو توزیع نمایش داده شود. |  | 1401-2294-31452 | 1401-01-30 | اعمال گردید.
4 | ارت بدنه تابلو UPS در مدرک نمایش داده شود. |  | 1401-2294-31452 | 1401-01-30 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Mar-22 |  |  |  |  | Date: