## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-SL-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0737 |  |  | Transmital Date: 26-Mar-2022
Document Title: UPS Single Line Diagram - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0737 |  |  | Transmital Date: 26-Mar-2022
[5 empty] | CRS No: PEDCO-CRS-BK-W007S-PEDCO-110-EL-SL-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised after finalizing or minor comments on Calculation Note For UPS System. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | مدرک محاسباتی UPS بر اساس بارهای اعلامی بخش ابزاردقیق ویرایش شده است. همچنین فیدرهای این مدرک مطابق با فیدرهای لیست بار ابزادرقیق می باشد. در صورت هرگونه نغییر در مدرک محاسباتی، این مدرک بازنگری خواهد شد.
2 | According to our telephone conversation, a separate sheet shall be added and 110AC distribution borad with all related feeders including incoming and outgoing feeders shall be shown. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | مطابق با بارهای ارائه شده در ترنسمیتال 852 که مربوط بعه بخش ابزاردقیق می باشد، خروجی ها در نظر گرفته شده است.
3 | Following items shall be added as notes: - Interlocks will be provided to inhibit battery boost charge if battery room ventilation is out of service. -Automatic battery isolation facility shall be provided for incoming MCCB of battery bank. incoming MCCB of battery bank shall be open when F&G system send battery insulation signal to the UPS. -An earth fault monitoring shall be considered for every 10 feeders for easy of finding faulty branch. -Metering and protection system shall be completed based on ac ups specification and detailed information shall be indicated On vendor drawing. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | موارد مطروحه در مدرک اضافه گردید.
4 | Some technical characteristics of equipment shall be added and specified on single line diagram such as rated voltage/short circuit level/rated current of 110AC distribution board, capacity/back up time/number and type of battery. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | این مدرک بر اساس مدرک ارسالی کارفرما در نامه شماره 375310 به روزرسانی شده است. علاوه بر این در نوت شماره 8 اشاره شده است که سازنده موظف به تعیین دقیق ظرفیت تجهیزات می باشد.
5 | The body of panels shall be earthed directly from two point. It shall be shown. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | علاوه بر اینکه ارت بدنه و تابلوی Distribution در مدرک نشان داده شده است، نوت شماره 13 نیز به این موضوع اشاره دارد.
6 | According to our telephone conversation, related note for cable size, type and tag shall be added. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | نوت شماره 6 به این موضوع اختصاص داده شده است.
7 | Battery limit of fuse box and battery bank and cable between them shall be shown. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | این مدرک بر اساس مدرک ارسالی کارفرما در نامه شماره 375310 به روزرسانی شده است.
8 | According to meeting date 1400.12.22 at PEDCO office, regarding to control system will be considered redundancy, so for each control system shall be considered two feeders instead of one feeder. |  | BK-SUR-ENG-ELE-01-03698 | 2022-03-30 | این مدرک بر اساس مدرک ارسالی کارفرما در نامه شماره 375310 به روزرسانی شده است.
fh
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Mar-22 |  |  |  |  | Date: