## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 8
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | DT | 0013 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | SEP. 2022 |  | IFA |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | NOV.2021 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  |  | F0Z-708844
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 8
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | DT | 0013 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Notes (1)
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 8
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0013 | D01
General Notes
Rev
| 1. | The Asterisk * denotes information and/or confirmation required from VENDOR.
| 2. | Deleted
| 3. | VENDOR shall include for the services of a independent verification body for mechanical design, stage inspection, testing and
stamping of the equipment (if possible).
| 4. | Painting and coating (internal & external) shall be as per project 'Specification for Painting', Doc. No. BK-GNRAL-PEDCO-000-PI-SP-0006.
D01 | 5. | Flanges shall comply with ASME B16.5. Nozzle bolt holes shall straddle the natural centrelines for horizontal nozzles.
VENDOR to confirm maximum allowable nozzle loads and moments (RF: Raised Face, WN: Welding Neck)
| 6. | All reinforcement pads shall have 1/4" (6mm) tell-tale hole and 1/8" (3mm) vent hole as per Standard Detail Drawing For Pressure Vessels
and Heat Exchangers', Doc. No. BK-GNRAL-PEDCO-000-ME-DW-0001".
| 7. | Manways shall be supplied complete with blind flange, external grab handles, internal grab handle and ladder rungs, nuts, bolting, gasket and
proof load test davits. Davits shall be proof load tested on the vessels to 1.5 x Safe Working Load (SWL) and shall be marked accordingly.
| 8. | All external bolts and nuts shall be hot dip galvanized. Internal bolts and nuts shall be stainless steel.
| 9. | Loads at support base, Shall be calculated and determined by vendor.
| 10. | Access Ladder & Platform to be considered .
D01 | 11. | Deleted
| 12. | All material, corrosion allowance and their suitability for the process fluid at design pressure and temperature to be confirmed by vendor.
D01 | 13. | Deleted
D01 | 14. | All nozzle locations and orientations to be finalized later.
| 15. | Instrumentation items are excluded from vendor's scope of supply.
| 16. | Any changes in material of construction, location & orientation of the nozzles shall be confirmed by client.
| 17. | All materials shall be new and unused.
| 18. | Fabrication tolerances for vessel shall be in accordance with requirement of ASME code.
| 19. | Location and number of lifting lugs on vessels shall be specificed on VENDOR drawing.
| 20. | All items shall be clearly match marked against vessel drawings to facilitate erection.
D01 | 21. | Deleted
| 22. | Vendor shall supply details of all welding connections and give general specification of used materials.
| 23. | For equipment requiring PWHT, final inspection and acceptance by the CLIENT or its nominated representative shall only be undertaken against
NDE after PWHT. All weldings shall be made before vessel heat treatment (if any).
D01 | 24. | Equipment packaging, preparation for shipment and delivery shall be in accordance with the project Packing, Marking, Transportation Procedure
Doc. No. "BK-GNRAL-PEDCO-000-QC-PR-0045".
| 25. | Specified accessories and attachments shall be supplied by vendor.
| 26. | Gasket shall be spiral wound type, graphite filled with inner ring and outer ring S.S.316
D01 | 27. | Deleted
D01 | 28. | Deleted
D01 | 29. | Two M12 earthing lugs shall be provided on vessel support. Material of Earthing lugs shall be S.S. 316
D01

## Notes (2)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 8
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0013 | D01
General Notes (Cont'd)
Rev
| 30. | For standard detail of Earth lug execution refer to the Project "Standard Detail Drawing For Pressure Vessels and Heat Exchangers
Doc. No. BK-GNRAL-PEDCO-000-ME-DW-0001". Projection of Horizontal & Vertical nozzles is from tengent line and centerline respectively.
| 31. | Elliptical heads shall be Ultrasonic Tested for LAMINATION after forming.
| 32. | The projection of equipment's nozzles should be considered as per 'Standard Detail Drawing For Pressure Vessels and Heat Exchangers',
Doc. No. BK-GNRAL-PEDCO-000-ME-DW-0001".
| 33. | The elevation of equipment's nozzels should be specified as follows :
I. For vertical vessels : from bottom T.L.
II. For horizontal vessels : from Left T.L.
| 34. | Nozzles and flanges shall be suitably supported and reinforced based on nozzle loads provided in project Specification for Pressure Vessels,
Document No. BK-GNRAL-PEDCO-000-ME-SP-0001.
| 35. | Prior to sealing the vessel for shipping and storage, the inside surface of the equipment shall be 100% visually inspected. Internal
surfaces shall be clean and thoroughly dried. The CLIENT or its nominated representative shall witness the cleanliness of internal
surfaces. Flange faces shall be protected by wooden or plastic dummy flanges.
D01 | 36. | Minimum requirement for pre-commissioning, commissioning, start up and two years operation shall be in accordance with document
E&C-QC-SP-1.
| 37 | Lifting Lugs / trunnions shall be provided to facilitate a single point lift. If a single point lift cannot be achieved without the use of a lifting
beam, then VENDOR shall provide a suitable, certified, lifting beam.
| 38. | Design pressure specified is at top of vessels. VENDOR design shell include static head for vessels flooded with specific gravity of
the handled liquid.
| 39. | VENDOR is to maximize shop fabrication based on the following transportation limits:
- Maximum weight: 96 tonnes
- Maximum load per axle: 12 tonnes
- Maximum length: 50.0 m
- Maximum width: 5.0 m
- Maximum height: 5.2 m
For items with dimensions and weights greater than the road capacity specified above, VENDOR may be required to split the package
into several components.
| 40. | All external attachments directly welded to the pressure part shall be the same material as vessel grade.
| 41. | Thickness indicated on this DWG are minimum. Vendor shall check and guarantee them on strength as per code and specification.
| 42. | All dimensions shown are in mm unless otherwise indicated. All nozzle sizes are in inch.
D01 | 43. | Deleted
D01 | 44. | DEMISTER specification will be finilized latter.
| 45. | The material shall be in compliance with NACE MR0175/ISO15156 and Specification For Material Requirements in Sour service
Document No. BK-GNRAL-PEDCO-000-PI-SP-0008.
| 46. | Welded carbon and carbon manganess steels for vessel shall comply with the following :
Carbon content shall not exceed 0.23%.
Based on the ladel analysis, below equation shall be satisfied.
Ceq. = C+MN/6+(Cr+Mo+V)/5+(Cu+Ni)/15 < 0.42 %
| 47. | All carbon steel material shall be fully killed, fine grain treated and supplied in the normalized condition.
D01 | 48. | The Vendor shall be fully responsible for the complete mechanical design, preparing calculation book and supply of the vessel.
D01

## Sheet 1
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: | [6 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  |  | نسخه |  |  | شماره صفحه: 5 از 8
9184 – 073 - 053 | [6 empty] | BK | GCS |  | PEDCO | 120 | ME |  | DT |  | 0013 |  |  | D01
Mechanical Data Sheets For Fuel Gas K.O. Drum (V-2205) / sheet 1 of 4
Rev | DATA SHEET | [21 empty] | Rev
| 1 | Description | : |  | Fuel Gas K.O. Drum
| 2 | Tag No. | : |  | V-2205 | [7 empty] | Quantity |  |  |  | : | 1 |  | Set
| 3 | Type | : |  | Pressure Vessel
| 4 | Process Design Data
| 5 | Contents | [10 empty] | Corrosive / Erosive | [8 empty] | CO2, H2S
| 6 | Operating Temp. |  |  | (oC) | 18.88 -36.78 | [6 empty] | Liquid Flow |  |  |  |  | (kg/h)
| 7 | Operating Press. |  | (barg) |  | 4.9 | [6 empty] | Vap. Molec. Weight |  |  |  |  | (kg/kmol)
| 8 | Gas Flow | (kg/h) | [9 empty] | Liquid Sp. Gravity | [8 empty] | 0.005771
| 9 | Liquid Viscosity |  | (cP) | [8 empty] | Service: | [8 empty] | Sour Service
| 10 | Mechanical Design Data
| 11 | Design Temp. | (oC) |  |  | 85 | [6 empty] | Vessel Orientation | [8 empty] | Vertical
| 12 | Design Press. | (barg) |  |  | 9 | [6 empty] | HHLL |  |  |  |  | (mm) |  |  |  | 1100 | D01
| 13 | Test Press. | (barg) |  |  | Per Code & Specification | [6 empty] | Nor. Liquid Vol. |  |  |  |  | (m3)
D01 | 14 | Internal Vacuum |  | (barg) |  | F.V. | [6 empty] | In. Dia. Of Boots |  |  |  |  | (mm) |  |  |  | N/A
| 15 | In. Dia. of Shell |  | (mm) |  | 438 | [6 empty] | Boot Length |  |  |  |  | (mm) |  |  |  | N/A
D01 | 16 | Tan/Tan Dim. | (mm) |  |  | 2950 | [6 empty] | Boot Head Type | [8 empty] | N/A
| 17 | Vessel Head Type |  |  |  | 2:1 elliptical + flange | [6 empty] | Corr. Allowance |  |  |  |  | (mm) |  |  |  | 6
D01 | 18 | Shell Wall Thk. | (mm) |  |  | * (See DWG) | [6 empty] | Joint Efficiency | [8 empty] | 0.85 (Shell) / 1 (Head) | D01
D01 | 19 | Head Wall Thk. | (mm) |  |  | * (After Forming) | [6 empty] | Ambient Temp. |  |  |  |  | (oC)
D01 | 20 | Seismic Design |  |  |  | Site Class: D, Code: ASCE 7-10 | [6 empty] | MDMT |  |  |  |  | (oC) |  |  |  | 3.24
D01 | 21 | Wind Design |  |  |  | Speed: 120 Km/hr (Max.), Code: ASCE 7-10 | [6 empty] | Insulation Required | [8 empty] | No
| 22 | Materials
D01 | 23 | Code |  |  |  |  | ASME II / ASTM | [5 empty] | Nozzle Necks:
D01 | 24 | Shell |  |  |  |  | A 106 Gr B (18" Pipe, Sch. STD) | [7 empty] | Pipes | [5 empty] | A 106 Gr.B N |  | D01
D01 | 25 | Heads |  |  |  |  | A 516 Gr. 60 N | [7 empty] | Plates | [5 empty] | A 516 Gr.60 N |  | D01
D01 | 26 | Lining / Cladding | [12 empty] | Forgings | [5 empty] | A 105 N |  | D01
D01 | 27 | Leg / Pad |  |  |  |  | A 516 Gr.60 N / A 283 Gr. C | [5 empty] | Flanges | [7 empty] | A 105 N |  | D01
| 28 | Platform Gratings |  |  |  |  | Hot Dip Galvanized C.S. | [5 empty] | Fittings | [7 empty] | A 234 Gr. WPB |  | D01
| 29 | Gaskets |  |  |  |  | Note 26 | [5 empty] | External Bolts | [7 empty] | A 193 Gr. B7 |  | D01
D01 | 30 | Lifting Lugs |  |  |  |  | A 516 Gr.60 N / A 283 Gr. C | [5 empty] | External Nuts | [7 empty] | A 194 Gr. 2H |  | D01
D01 | 31 | Reinforcing Pads |  |  |  |  | A 516 Gr.60 N | [5 empty] | Internal (Removable) | [7 empty] | S.S. 316
| 32 | Ladder & Platform |  |  |  |  | C.S. | [5 empty] | Internal (Fixed) | [7 empty] | A 516 Gr.60 N |  | D01
| 33 | Name Plate |  |  |  |  | S.S. 316
34
| 35 | REFERENCE STANDARDS & DOCUMENTS
| 36 | Mechanical Design Code | [10 empty] | ASME Sec VIII Div 1, IPS-G-ME-150
| 37 | Specification for Pressure Vessels | [10 empty] | BK-GNRAL-PEDCO-000-ME-SP-0001
| 38 | Process Basis of Design | [10 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001
| 39 | Piping & Instrument Diagram (P&ID) | [10 empty] | BK-GCS-PEDCO-120-PR-PI-0022
| 40 | Specification for Painting | [10 empty] | BK-GNRAL-PEDCO-000-PI-SP-0006
| 41 | Specification for Insulation | [10 empty] | BK-GNRAL-PEDCO-000-PI-SP-0019
| 42 | Specification For Material Requirements in Sour service | [10 empty] | BK-GNRAL-PEDCO-000-PI-SP-0008 (Note 45)
43
| 44 | Fabrication and Inspection Requirements
| 45 | Inspection Authority |  |  |  |  | TPI & Client
| 46 | Material Certification |  |  |  |  | In Accordance with BS EN 10204:2004, Type 3.1, Minimum for Pressure Containing and Attachments
| 47 | Hydro Test Medium |  |  |  |  | Water | [5 empty] | Hydro Test Procedure | [7 empty] | Yes;Per Code & Spec. Requirements
| 48 | Post Weld Heat Treatment |  |  |  |  | Yes, Process Reason | [5 empty] | PT | [7 empty] | 100%
| 49 | MT |  |  |  |  | 100 % on Lifting Lug Fillet Welds | [5 empty] | UT | [7 empty] | Yes;Per Code & Spec. Requirements
| 50 | RT |  |  |  |  | Spot | % | On T-Joints and Head Joints Butt-Welds,
| 52 | [5 empty] | 100 | % | On Nozzle Neck to Flange & Fabricated Nozzle Neck Longitudinal Butt-Welds,
| 53 | RT Report |  |  |  |  | Yes; Per Code & Spec. Requir. | [5 empty] | PT Report | [7 empty] | Yes;Per Code & Spec. Requirements
| 54 | MT Report |  |  |  |  | Yes; Per Code & Spec. Requir. | [5 empty] | UT Report | [7 empty] | Yes;Per Code & Spec. Requirements
| 55 | Fabrication Quality Control Plan (With Offer) | [10 empty] | Yes
| 56 | Welding Procedure Review / Approval | [10 empty] | Yes
| 57 | Surface Preparation & Coating | [10 empty] | Specification for Painting Doc. No. "BK-GNRAL-PEDCO-000-PI-SP-0006"
| 58 | [11 empty] | Specification for Lining Doc. No: "BK-GNRAL-PEDCO-000-PI-SP-0007"
59
60
61
62
63
D01
D01

## Sheet 2
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: | [6 empty] | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 6 از 8
9184 – 073 - 053 | [6 empty] | BK |  | GCS | PEDCO | 120 |  | ME |  | DT | 0013 |  | D01
Mechanical Data Sheets For Fuel Gas K.O. Drum (V-2205) / sheet 2 of 4
Rev. | ACCESSORIES , NOZZLES LIST & LOADS @ BASE | [23 empty] | Rev.
| 1 | Accessories & Attachments (Note 25)
| 2 | Supporting Leg | [9 empty] | YES |  | Name Plate Bracket | [9 empty] | YES
| 3 | Access Ladder & Platform (Note 10) | [9 empty] | YES |  | Name Plate | [9 empty] | YES
| 4 | Insulation Support | [9 empty] | NO |  | Earthing Lug (Note 30) | [9 empty] | YES
| 5 | Insulation | [9 empty] | NO |  | Tailing Lug | [9 empty] | NO
| 6 | Insulation Cover | [9 empty] | NO |  | Cathodic Protection (Sacrificial Anodes) | [9 empty] | NO | D01
| 7 | Fireproofing Support | [9 empty] | NO |  | Anchor Bolts | [9 empty] | NO | D01
| 8 | Lifting Lugs | [9 empty] | YES |  | Instrumentations | [9 empty] | NO
| 9 | Internal Supports | [9 empty] | YES |  | Skid | [9 empty] | NO
| 10 | Internal Impingement Baffle | [9 empty] | YES |  | Vortex Breaker | [9 empty] | YES
| 11 | Internal Demistier Pad (Note 44) | [9 empty] | YES |  | Davit for Body Flange | [9 empty] | YES | D01
D01 | 12 | Internal Lining | [9 empty] | YES
13
14
15
16
17
| 18 | Nozzles List * (Note 1)
| 19 | Mark |  | Qty. |  | Description |  |  |  | Pipe |  |  |  |  | Flange |  |  |  | Proj. | (mm) | Reinforcement |  | Remarks
| 20 | [8 empty] | Size | Thk. |  | Sch. |  | Type | Rate. | Face |  | (Note 32) |  | Thk. | O.D.
D01 | 21 | A |  | 1 |  | Inlet |  |  |  | 2" |  |  |  |  | WN | #150 | RF |  | 428.5
D01 | 22 | B1 |  | 1 |  | Gas Outlet |  |  |  | 2" |  |  |  |  | WN | #150 | RF |  | See DWG
D01 | 23 | B2 |  | 1 |  | Liquid Outlet |  |  |  | 2" |  |  |  |  | WN | #150 | RF |  | 314.25
D01 | 24 | Deleted
D01 | 25 | H |  | 1 |  | Handhole |  |  |  | 8" |  |  |  |  | WN | #150 | RF |  | 478.5 |  | * | * | Note 6
D01 | 26 | S |  | 1 |  | Utility Connection |  |  |  | 2" |  |  |  |  | WN | #150 | RF |  | 428.5
D01 | 27 | P1 |  | 1 |  | Pressure Gauge |  |  |  | 2" |  |  |  |  | WN | #300 | RF |  | 428.5
D01 | 28 | P 2,3 |  | 2 |  | PDG |  |  |  | 2" |  |  |  |  | WN | #300 | RF |  | 428.5
D01 | 29 | PSV |  | 1 |  | Pressure Safety Valve |  |  |  | 2" |  |  |  |  | WN | #150 | RF |  | 428.5
D01 | 30 | L 1,2 |  | 2 |  | Stand Pipe |  |  |  | 3" |  |  |  |  | WN | #150 | RF |  | 428.5
D01 | 31 | L 3,4 |  | 2 |  | Level Transmitter |  |  |  | 2" |  |  |  |  | WN | #300 | RF |  | 428.5
D01 | 32 | V |  | 2" |  | Vent |  |  |  | 2" |  |  |  |  | WN | #150 | RF |  | See DWG
33
34
35
36
37
38
39
40
41
42
| 43 | Wind and Seismic Loads at Base * Note(9)
| 44 |  | Load Condition |  | Empty Condition | [5 empty] | Operating Condition | [6 empty] | Testing Condition
45
| 46 |  |  |  | Max. Shear @ Base (Kg) |  |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg) | Max. Shear @ Base (Kg) |  |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg) |  | Max. Shear @ Base (Kg) |  | Max. Moment @ Base (Kg.m) |  | Weight (Kg)
47
| 48 |  | Load Type
49
50
| 51 | WIND
52
| 53 | SEISMIC
54
55
56
57
58
59
60
61
62
63
65
D01
D01

## Sheet 3
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 8
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | ME | DT | 0013 | D01
Mechanical Data Sheets For Fuel Gas K.O. Drum (V-2205) / sheet 3 of 4
Sketch
All dimensions are in mm.

## Sheet 4
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث ردیف تراکم گاز در ایستگاه جمع آوری بینک
MECHANICAL DATA SHEETS FOR FUEL GAS K.O. DRUM
شماره پیمان: | [6 empty] | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 8 از 8
9184 – 073 - 053 | [6 empty] | BK | GCS |  | PEDCO |  | 120 | ME |  | DT | 0013 |  | D01
Mechanical Data Sheets For Fuel Gas K.O. Drum (V-2205) / sheet 4 of 4
Rev. | WEIGHT | [21 empty] | Rev.
| 1 | WEIGHT CONTROL DATA SHEET SI UNIT * | [12 empty] | 1/1
2
3
4
5
| 6 | Service |  | : |  | Fuel Gas K.O. Drum | [8 empty] | Location |  | : | Bushehr (Binak Oilfield) |  |  |  |  | D01
| 7 | Type |  | : | [10 empty] | Quotation No. |  | :
| 8 | No. trains |  | : | [10 empty] | Serial No. |  | :
| 9 | No. stages |  | :
| 10 | Supplier |  | :
| 11 | Manufacturer |  | :
| 12 | Model |  | :
13
| 14 | Note: Information to be completed by equipment vendor.
15
| 16 | Total weight (kg) *
| 17 | Fabrication |  |  | Erection |  |  |  | Operation |  |  |  |  | Hydrostatic Test |  |  |  | Removable internal |  |  | Ladder & Platform
18
19
20
21
22
| 23 | WEIGHT AND C OF G DATA REQUIRED *
| 24 | CONDITION |  |  |  | WEIGHT ACCURACY % |  |  |  |  | WEIGHT (kg) |  |  |  |  | CENTER OF GRAVITY (mm)
| 25 | [14 empty] | X |  |  | Y |  |  | Z
| 26 | Dry
27
28
29
| 30 | SKETCH
31
32
33
| 34 | [13 empty] | ASME BPVC VIII, DIV.1
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
| 52 | NOTES
| 53 | 1) | All lifting points to be load tested and certified.
| 54 | 2) | Any spreader beam to be load tested and certified.
| 55 | 3) | Lifting / rigging plan for skid mounted equipment to be provided by the Vendor.
56
57
58
59
60
61
62
63