## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-PY-0001_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0935 |  |  | Transmital Date: 11 May 2022
Document Title:Control Room Layout & Arrangement Drawing - Extension of Binak B/C Manifold |  |  |  |  | EPC Contractor Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-0935 |  |  | Transmital Date: 11 May 2022
[5 empty] | CRS No: PEDCO-BK-W007S-PEDCO-110-IN-PY-0001_D00 |  |  | CRS Status: | C3
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ابعاد NEW DCS و NEW ESD Pannels درج شود. |  | - | 2022-05-28 | مطابق خواست آن شرکت محترم اعمال شد.
2 | با توجه به ادعاي كارفرما در جلسه Model Review استفاده از ترنچ جديد درخواست شده است در اين خصوص شفاف سازي صورت پذيرد. |  | - | 2022-05-28 | با توجه به محدودیت های سایت موجود در اتاق کنترل امکان ایجاد ترنج جدید در اتاق کنترل نمیباشد.
3 | Reference Document و Legend مشخص شود. |  | - | 2022-05-28 | مطابق خواست آن شرکت محترم اعمال شد.
4 | در رابطه با تغذيه پنل FACP و ارتباطش با ديتكتورها شفاف سازي گردد. |  | - | 2022-05-28 | تغذیه پنل از طریق باتری های 24VDC میباشد که در اتاق همجوار سوییچ گیر جاسازی میشود .در این نقشه نوت اضافه شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 28 May 2022 |  |  |  |  | Date: