## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0003 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR ESD SYSTEMS نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | SEP.2022 |  | AFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | MAY.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number:'F0Z-708969
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0003 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 |  | X | X | [5 empty] | 73
10 |  | X | X | [5 empty] | 74
11 |  |  | X | [5 empty] | 75
12 |  |  | X | [5 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 12
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 | IN | LI | 0003 | D02
REFERENCES:
|  | Symbol & Legend For PFD and P&ID | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0001_D02
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0002_D04
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0003_D04
|  | P&ID - Slug Catcher System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D04
|  | P&ID - Gas Compression Inlet Knock Out Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D04
|  | P&ID - 1st Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D04
|  | P&ID - 1st Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D04
|  | P&ID - 1st Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0008_D04
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D04
|  | P&ID - 2nd Stage Gas Compression Compressors | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D04
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011_D04
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D04
|  | P&ID - Gas Compression Dehydration Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013_D04
|  | P&ID - Lean Glycol Storage Tank | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D04
|  | P&ID - Instrument & Plant Air System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D04
|  | P&ID - Nitrogen Generation System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D04
|  | P&ID - Close Drain System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0017_D04
|  | P&ID - Corrosion Inhibitor Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0018_D04
|  | P&ID - Methanol Injection Package | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0019_D04
|  | P&ID - LP Flare System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0020_D04
|  | P&ID - Oily Water Sewer | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0021_D04
|  | P&ID - Fuel Gas System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D04
|  | P&ID - Diesel Oil System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D04
|  | P&ID - Potable Water System | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0024_D04
|  | P&ID - Glycol Sump Drum | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D04
|  | P&ID - Fire Water Network | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0001_D01
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [7 empty] | BK-GCS-PEDCO-120-SA-PI-0002_D02
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [7 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D03
|  | Data Sheets For ESD Console/F&G Matrix Panel | [7 empty] | BK-GCS-PEDCO-120-IN-DT-0017_D00
|  | ESD Level Hierarchy | [7 empty] | BK-GCS-PEDCO-120-IN-DG-0003_D00
NOTES:
| NOTE 1 : |  | ALL OF ANALOGE TRANSMITTER SHALL BE CONSIDERED INTRINSICALLY SAFE (EEXIA) & ALL OF DIGITAL TRANSMITTER ARE NON INTRINSICALLY SAFE (EEXD).
| NOTE 2 : |  | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
| NOTE 3 : |  | ESD EQUIPMENT & ALL OF EQUIPMENT THAT IS ASSIGNED IN A CONTROL LOOP, ARE REDUNDANT.
| NOTE 4 : |  | ALL I/Os REQUIRED FOR DEHYDRATION PACKAGE (PK-2101) WILL BE ADDED TO THIS SUMMARY AS PER VENDOR DATA LATER.
| NOTE 5 : |  | ALL I/Os REQUIRED FOR ESD SHALL BE SHOWN IN DCS BY SERIAL LINK.
D02

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 12
9184 – 073 - 053 | [5 empty] | BK | GCS |  | PEDCO | 120 | IN | LI | 0003 | D02
ESD I/O SUMMERY COUNT
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 60 |  | 72 | NOTES 1,2,3,4 | 72
| 2 |  | AI-IS-NR |  | IS | NR |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 3 |  | AO-IS-R |  | IS | R |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 4 |  | AO-IS-NR |  | IS | NR |  | ANALOGUE OUTPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 5 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 46 |  | 56 | NOTES 1,2,3,4 | 55.2
| 6 |  | DI-NIS-NR |  | NIS | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
| 7 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 91 |  | 110 | NOTES 1,2,3,4 | 109.2
| 8 |  | DO-NIS-NR |  | NIS | NR |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 0 |  | 0 | NOTES 1,2,3,4 | 0
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT
D02

## IO List for ESD System
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR ESD SYSTEMS
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK | GCS | PEDCO | 120 |  | IN |  | LI |  | 0003 |  |  | D02
I/O List For ESD System
ITEM | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | I/O TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[14 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
1 | EZSC-2101 | ESDV Limit Switch Close | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
2 | EZSO-2101 | ESDV Limit Switch Close | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
3 | ESOV-2101 | Solenoid Valve | TO INLET K.O. DRUM (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0002 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
4 | EZSC-2102 | ESDV Limit Switch Close | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
5 | EZSO-2102 | ESDV Limit Switch Close | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
6 | ESOV-2102 | Solenoid Valve | TO SLUG CATCHER (V-2104) |  | BK-GCS-PEDCO-120-PR-PI-0003 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
7 | PIT-2111 | Pressure Indicator Transmitter | From Gas Pig Receiver (PR-2102) |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D02 MODIFIED
8 | LIT-2112 | Level Indicator Transmitter | V-2104 |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
9 | ESOV-2111 | Solenoid Valve | From V-2104 / To Degassing Vessel (V-2106) |  | BK-GCS-PEDCO-120-PR-PI-0004 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
10 | LIT-2115 | Level Indicator Transmitter | TK-2101 |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
11 | PIT-2115 | Pressure Indicator Transmitter | FROM P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
12 | PIT-2114A | Pressure Indicator Transmitter | TO P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
13 | PIT-2114B | Pressure Indicator Transmitter | TO P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
14 | PIT-2116A | Pressure Indicator Transmitter | CDH-112-0012-CN05-3"-PT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
15 | PIT-2116B | Pressure Indicator Transmitter | CDH-112-0013-CN05-3"-PT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
16 | ESD-P-2111-A | Trip Command | P-2101A |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
17 | ESD-P-2111-B | Trip Command | P-2101B |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
18 | EZSC-2112 | ESDV Limit Switch Close | FROM P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
19 | EZSO-2112 | ESDV Limit Switch Close | FROM P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
20 | ESOV-2112 | Solenoid Valve | FROM P-2101A/B TO BINAK PRODUCTION UNIT |  | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
21 | ESOV-2113 | Solenoid Valve | From V-2105 /To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
22 | LIT-2117 | Level Indicator Transmitter | (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
23 | LIT-2118 | Level Indicator Transmitter | (V-2105) |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X |  |  | D02 MODIFIED
24 | PIT-2116 | Pressure Indicator Transmitter | FROM SLUG CATCHER DRUM (V-2104) To V-2105 |  | BK-GCS-PEDCO-120-PR-PI-0005 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
25 | ESOV-2121A | Solenoid Valve | From 1ST Sttage Gas Compression Suction Manifold To V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
26 | LIT-2122A | Level Indicator Transmitter | V-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
27 | ESOV-2122A | Solenoid Valve | From V-2101-ATo Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
28 | ESOV-2121B | Solenoid Valve | FROM 1ST STAGE GAS COMPRESSION SUCTION MANIFOLD To V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
29 | LIT-2122B | Level Indicator Transmitter | V-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
30 | ESOV-2122B | Solenoid Valve | From V-2101-BTo Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
31 | ESOV-2121C | Solenoid Valve | From 1ST Sttage Gas Compression Suction Manifold To V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
32 | LIT-2122C | Level Indicator Transmitter | V-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
33 | ESOV-2122C | Solenoid Valve | To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
34 | PIT-2122A | Pressure Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101A) To C-2101-A |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
35 | PIT-2125A | Pressure Indicator Transmitter | Outlet Comp. C-2101-A / TO 1ST STAGE AIR COOLER (AE-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
36 | TIT-2124A | Temperature Indicator Transmitter | Outlet Comp. C-2101-A / TO 1ST STAGE AIR COOLER (AE-2101A) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
37 | ESDR2A-C-2101-A | Trip Command With Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X
38 | ESDR2-C-2101-A | Trip Command Without Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X
39 | ESD2A-C-2101-A | Trip Alarm With Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
40 | ESD2-C-2101-A | Trip Alarm Without Depressurizing | inlet Comp. C-2101-A (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (1 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
41 | PIT-2122B | Pressure Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101B) To C-2101-B |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X | X |  | X
42 | PIT-2125B | Pressure Indicator Transmitter | Outlet Comp. C-2101-B / TO 1ST STAGE AIR COOLER (AE-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
43 | TIT-2124B | Temperature Indicator Transmitter | Outlet Comp. C-2101-B / TO 1ST STAGE AIR COOLER (AE-2101B) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
44 | ESDR2A-C-2101-B | Trip Command With Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X
45 | ESDR2-C-2101-B | Trip Command Without Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X
46 | ESD2A-C-2101-B | Trip Alarm With Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
47 | ESD2-C-2101-B | Trip Alarm Without Depressurizing | inlet Comp. C-2101-B (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (2 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
48 | PIT-2122C | Pressure Indicator Transmitter | From 1ST Stage Gas Comp. Suction Drum (V-2101C) To C-2101-C |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X | X |  | X
49 | PIT-2125C | Pressure Indicator Transmitter | Outlet Comp. C-2101-C / TO 1ST STAGE AIR COOLER (AE-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
50 | TIT-2124C | Temperature Indicator Transmitter | Outlet Comp. C-2101-C / TO 1ST STAGE AIR COOLER (AE-2101C) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
51 | ESDR2A-C-2101-C | Trip Command With Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X
52 | ESDR2-C-2101-C | Trip Command Without Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | UCP-C-2101 |  | * | * | * | * | * | * | * | * | [5 empty] | X
53 | ESD2A-C-2101-C | Trip Alarm With Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
54 | ESD2-C-2101-C | Trip Alarm Without Depressurizing | inlet Comp. C-2101-C (UCP-C-2101) |  | BK-GCS-PEDCO-120-PR-PI-0007 (3 of 3) |  |  | DI-NIS-R |  | UCP-C-2101 |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
55 | VSHH-2121A | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
56 | VSHH-2122A | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
57 | ESD-AE-2101-A-1 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
58 | ESD-AE-2101-A-2 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
59 | TIT-2125A | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-A) |  | BK-GCS-PEDCO-120-PR-PI-0008 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X |  |  |  | X
60 | VSHH-2121B | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
61 | VSHH-2122B | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
62 | ESD-AE-2101-B-1 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
63 | ESD-AE-2101-B-2 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
64 | TIT-2125B | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-B) |  | BK-GCS-PEDCO-120-PR-PI-0008 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X |  |  |  | X
65 | VSHH-2121C | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
66 | VSHH-2122C | Vibration Switch | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
67 | ESD-AE-2101-C-1 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
68 | ESD-AE-2101-C-2 | Trip Command | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
69 | TIT-2125C | Temperature Indicator Transmitter | FROM 1ST Stage Gas Compressor Air Coolers (AE-2101-C) |  | BK-GCS-PEDCO-120-PR-PI-0008 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * | X |  |  |  | X
70 | LIT-2132A | Level Indicator Transmitter | V-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
71 | BSOV-2134A | Solenoid Valve | From V-2102-A To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
72 | ESOV-2131A | Solenoid Valve | From V-2102-A To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
73 | LIT-2132B | Level Indicator Transmitter | V-2102-B |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
74 | BSOV-2134B | Solenoid Valve | From V-2102-B To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
75 | ESOV-2131B | Solenoid Valve | From V-2102-B To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
76 | LIT-2132C | Level Indicator Transmitter | V-2102-C |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
77 | BSOV-2134C | Solenoid Valve | From V-2102-C To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
78 | ESOV-2131C | Solenoid Valve | From V-2102-C To Closed Drain Header |  | BK-GCS-PEDCO-120-PR-PI-0009 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
79 | PIT-2131A | Pressure Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102A) To C-2102-A |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
80 | PIT-2134A | Pressure Indicator Transmitter | from V-2102A To 2ND Stage Air Cooler (AE-2102A) |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
81 | TIT-2134A | Temperature Indicator Transmitter | from V-2102A To 2ND Stage Air Cooler (AE-2102A) |  | BK-GCS-PEDCO-120-PR-PI-0010 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
82 | PIT-2131B | Pressure Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102B) To C-2102-B |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
83 | PIT-2134B | Pressure Indicator Transmitter | from V-2102B To 2ND Stage Air Cooler (AE-2102B) |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
84 | TIT-2134B | Temperature Indicator Transmitter | from V-2102B To 2ND Stage Air Cooler (AE-2102B) |  | BK-GCS-PEDCO-120-PR-PI-0010 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
85 | PIT-2131C | Pressure Indicator Transmitter | From 2ND Stage Gas Comp. Suction Drum (V-2102C) To C-2102-C |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
86 | PIT-2134C | Pressure Indicator Transmitter | from V-2102C To 2ND Stage Air Cooler (AE-2102C) |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
87 | TIT-2134C | Temperature Indicator Transmitter | from V-2102C To 2ND Stage Air Cooler (AE-2102C) |  | BK-GCS-PEDCO-120-PR-PI-0010 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
88 | ESD-AE-2102-A-1 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
89 | ESD-AE-2102-A-2 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
90 | VSHH-2131A | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
91 | VSHH-2132A | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
92 | TIT-2136A | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-A) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
93 | BSOV-2132A | Solenoid Valve | From AE-2102-A To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
94 | ESOV-2133A | Solenoid Valve | From AE-2102-A To Gs Compression Dicharge Drum ( V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
95 | ESD-AE-2102-B-1 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
96 | ESD-AE-2102-B-2 | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
97 | VSHH-2131B | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
98 | VSHH-2132B | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
99 | TIT-2136B | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-B) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X |  |  | X
100 | BSOV-2132B | Solenoid Valve | From AE-2102-B To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
101 | ESOV-2133B | Solenoid Valve | From AE-2102-B To Gs Compression Dicharge Drum ( V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
102 | ESD-2131C | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
103 | ESD-2132C | Trip Command | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
104 | ESD-AE-2102-C-1 | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
105 | ESD-AE-2102-C-2 | Vibration Switch | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X
106 | TIT-2136C | Temperature Indicator Transmitter | FROM 2ND Stage Gas Compressor Air Coolers (AE-2102-C) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  | X |  |  | X
107 | BSOV-2132C | Solenoid Valve | From AE-2102-C To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
108 | ESOV-2133C | Solenoid Valve | From AE-2102-B To Gs Compression Dicharge Drum ( V-2103) |  | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
109 | BSOV-2141 | Solenoid Valve | FROM METHANOL HEADER To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
110 | XZSC-2142 | ESDV Limit Switch Close | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
111 | XZSO-2142 | ESDV Limit Switch Close | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
112 | ESOV-2142 | Solenoid Valve | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
113 | XZSC-2143 | ESDV Limit Switch Close | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
114 | XZSO-2143 | ESDV Limit Switch Close | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
115 | ESOV-2143 | Solenoid Valve | From V-2103 To Dehdration package (PK-2101) |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
116 | LIT-2142 | Level Indicator Transmitter | V-2103 |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
117 | ESOV-2144 | Solenoid Valve | From V-2103 To TO CLOSED DRAIN HEADER |  | BK-GCS-PEDCO-120-PR-PI-0012 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
118 | BSOV-2151 | Solenoid Valve | DEHYDRATION PACKAGE (PK-2101)To LP Flare Header |  | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
119 | LIT-2161 | Level Indicator Transmitter | TK-2102 |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
120 | ESD-P-2161-A | Trip Command | P-2103A |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
121 | ESD-P-2161-B | Trip Command | P-2103B |  | BK-GCS-PEDCO-120-PR-PI-0014 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
122 | EZSC-2131 | ESDV Limit Switch Close | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
123 | EZSO-2131 | ESDV Limit Switch Close | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  |  | D02 MODIFIED
124 | ESOV-2131 | Solenoid Valve | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
125 | PIT-2202 | Pressure Indicator Transmitter | Air Compressor Package (PK-C-2203 A/B) / AIR DRYER PACKAGE (PK-DR-2203 A/B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
126 | ESD-PK-C-2203 A | Trip Command | Air Compressor Package (PK-C-2203 A) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
127 | ESD-PK-C-2203 B | Trip Command | Air Compressor Package (PK-C-2203 B) |  | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
128 | PT-2201A | Pressure Transmitter | From Air Drayer Package (PK-DR-2203) TO INSTRUMENT HEADER |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
129 | PT-2201B | Pressure Transmitter | From Air Drayer Package (PK-DR-2203) TO INSTRUMENT HEADER |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
130 | PT-2201C | Pressure Transmitter | From Air Drayer Package (PK-DR-2203) TO INSTRUMENT HEADER |  | BK-GCS-PEDCO-120-PR-PI-0015 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
131 | PT-2211A | Pressure Transmitter | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
132 | PT-2211B | Pressure Transmitter | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
133 | PT-2211C | Pressure Transmitter | Air Compressor Package (PK-C-2204)/NITROGEN PACKAGE (PK-G-2204)/ NITROGEN RECEIVER (V-2204) |  | BK-GCS-PEDCO-120-PR-PI-0016 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
134 | PIT-2151 | Pressure Indicator Transmitter | NIT-112-0024-AN01-2"-PT |  | BK-GCS-PEDCO-120-PR-PI-0016 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
135 | LIT-2222 | Level Indicator Transmitter | V-2202 |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
136 | PIT-2222A | Pressure Indicator Transmitter | CDH-112-0032-AN07-2"-PT |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
137 | PIT-2222B | Pressure Indicator Transmitter | CDH-112-0033-AN07-2"-PT |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
138 | ESD-P-2211-A | Trip Command | P-2202-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
139 | ESD-P-2211-B | Trip Command | P-2202-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
140 | ESD-P-2222-A | Trip Command | P-2203-A |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
141 | ESD-P-2222-B | Trip Command | P-2203-B |  | BK-GCS-PEDCO-120-PR-PI-0017 (2 of 2) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
142 | ESD-PK-2207 | Trip Command | Corrosion Inhibitor Package (PK-TK-2207)/CORROSION INHIBITOR PACKAGE (PK-2207 A/B/C/D) |  | BK-GCS-PEDCO-120-PR-PI-0018 |  |  | DO-NIS-R |  | ESD |  | PK-2207 |  | * | * | * | * | * | * | * | * | [5 empty] | X
143 | ESD-PK-2208 | Trip Command | Methanol Injection Tank (PK-TK-2208) |  | BK-GCS-PEDCO-120-PR-PI-0019 |  |  | DO-NIS-R |  | ESD |  | PK-2208 |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
144 | LALL-2241 | Level Alarm Low Low | Methanol Injection Tank (PK-TK-2208) |  | BK-GCS-PEDCO-120-PR-PI-0019 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
145 | ESD-P-2251A | Trip Command | P-2201 A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
146 | ESD-P-2251B | Trip Command | P-2201 B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X
147 | LIT-2252A | Level Indicator Transmitter | V-2201 |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
148 | LIT-2252B | Level Indicator Transmitter | V-2201 |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
149 | LIT-2252C | Level Indicator Transmitter | V-2201 |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  |  | X
150 | PIT-2251A | Pressure Indicator Transmitter | P-2201 A |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
151 | PIT-2251B | Pressure Indicator Transmitter | P-2201 B |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
152 | LIT-2253 | Level Indicator Transmitter | V-2201 |  | BK-GCS-PEDCO-120-PR-PI-0020 (2 of 3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
153 | ESOV-2272 | Solenoid Valve | From Inlet K.O. Drum (V-2105) To V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
154 | LIT-2272 | Level Indicator Transmitter | V-2205 |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * | X |  |  | X | X
155 | ESOV-2271 | Solenoid Valve | From Inlet K.O. Drum (V-2105) To TO CLOSED DRAIN HEADER |  | BK-GCS-PEDCO-120-PR-PI-0022 (1 of 1) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X
156 | PIT-2281 | Pressure Indicator Transmitter | P-2206 |  | BK-GCS-PEDCO-120-PR-PI-0023 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  |  | D02 MODIFIED
157 | ESD-P-2206 | Trip Command | P-2206 |  | BK-GCS-PEDCO-120-PR-PI-0023 |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
158 | ESOV-3101 | Solenoid Valve | ESDV-3101 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
159 | PIT-3201A | Pressure Indicator Transmitter | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
160 | PIT-3201B | Pressure Indicator Transmitter | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
161 | PIT-3201C | Pressure Indicator Transmitter | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X
162 | ESDR 0-UPS | UPS FAILURE | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
163 | ESDR 0-F&G | CONFIRMED FLAMMABLE GAS IN HVAC INTAKE (COMMAND FROM F&G) | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
164 | ESD 0-EL1 | EMERGENCY + NORMAL POWER ISOLATION | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [6 empty] | X
165 | ESD 0-EL2 | UPS BATTERY ISOLATION | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | UPS CHARGER |  | * | * | * | * | * | * | * | * | [6 empty] | X
166 | ESDR 1A-F&G | CONFIRMED FLAMMABLE GAS IN PROCESS AREA (COMMAND FROM F&G) | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
167 | ESD 1A-EL1 | POWER ISOLATION IN PROCESS AREA | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | IRP |  | * | * | * | * | * | * | * | * | [6 empty] | X
168 | ESDR 1-EL1 | NETWORK POWER FAILURE SWITCH ACTIVATION | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | IRP |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
169 | ESDR 1-DC | DC CHARGER FAILURE | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | UPS CHARGER |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
170 | ESDR 1-PCS | PCS FAILURE | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
171 | ESDR 1-FLR | FLARE IGNITION FAILURE | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | DCS |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
172 | ESD 2A-F&G-A | CONFIRMED FIRE IN FIRE ZONE AREA (COMMAND FROM F&G)- TRAIN A | CONTROL ROOM |  | __ |  |  | DI-NIS-R |  | F&G |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
173 | ESD0-LAMP | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
174 | ESD1A-LAMP | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A) | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
175 | ESD2A-A-LAMP | TRAIN A SHUT DOWN WITH DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
176 | ESD2A-B-LAMP | TRAIN B SHUT DOWN WITH DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
177 | ESD2A-C-LAMP | TRAIN C SHUT DOWN WITH DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
178 | LAMP-ESD-INH | ESD INHIBIT LAMP | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
179 | LAMP-ESD-RST | ESD RESET LAMP | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
180 | ESD1-LAMP | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1) | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
181 | ESD2-A-LAMP | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
182 | ESD2-B-LAMP | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
183 | ESD2-C-LAMP | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING | ESD CONSOL |  | __ |  |  | DO-NIS-R |  | ESD |  | ESD CONSOL |  | * | * | * | * | * | * | * | * | [6 empty] | X
184 | ESD 3-A-LAMP | COMPRESSOR C-2101-A SHUTDOWN LAMP | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
185 | ESD 3-B-LAMP | COMPRESSOR C-2101-B SHUTDOWN LAMP | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
186 | ESD 3-C-LAMP | COMPRESSOR C-2101-C SHUTDOWN LAMP | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
187 | ESD0-PB | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
188 | ESD1A-PB | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
189 | ESD2A-A-PB | TRAIN A SHUT DOWN WITH DEPRESSURIZING (ESD2A-A) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
190 | ESD2A-B-PB | TRAIN B SHUT DOWN WITH DEPRESSURIZING (ESD2A-B) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
191 | ESD2A-C-PB | TRAIN C SHUT DOWN WITH DEPRESSURIZING (ESD2A-C) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
192 | ESD-INH | ESD INHIBIT SELECTOR SWITCH | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
193 | ESD-RST | RESET P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
194 | ESD1-PB | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
195 | ESD2-A-PB | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-A) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
196 | ESD2-B-PB | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-B) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
197 | ESD2-C-PB | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-C) P.B. | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X
198 | ESD 3-A-PB | COMPRESSOR C-2101-A SHUTDOWN PUSH BOTTOM | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
199 | ESD 3-B-PB | COMPRESSOR C-2101-B SHUTDOWN PUSH BOTTOM | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
200 | ESD 3-C-PB | COMPRESSOR C-2101-C SHUTDOWN PUSH BOTTOM | ESD CONSOL |  | __ |  |  | DI-NIS-R |  | ESD CONSOL |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X |  | D02 MODIFIED
201 | ESDI 0-EX | EXISTING SYSTEM ESD 0 status | EXISTING SYSTEM |  | __ |  |  | DI-NIS-R |  | EXISTING SYSTEM |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED
202 | ESDI 1-EX | EXISTING SYSTEM ESD 1 status | EXISTING SYSTEM |  | __ |  |  | DI-NIS-R |  | EXISTING SYSTEM |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED
203 | ESDI 1A-EX | EXISTING SYSTEM ESD 1A status | EXISTING SYSTEM |  | __ |  |  | DI-NIS-R |  | EXISTING SYSTEM |  | ESD |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED
204 | ESDI 0- NEW | ESD 0 status | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
205 | ESDI 1- NEW | ESD 1 status | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
206 | ESDI 1A- NEW | ESD 1A status | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | EXISTING SYSTEM |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
207 | ESDI 0-DCS | ESD 0 status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
208 | ESDI 1-DCS | ESD 1 status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
209 | ESDI 1A-DCS | ESD 1A status in DCS | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
210 | ESDI 2-A-DCS | ESD 2 status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
211 | ESDI 2-B-DCS | ESD 2 status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
212 | ESDI 2-C-DCS | ESD 2 status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
213 | ESDI 2A-A-DCS | ESD 2A status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
214 | ESDI 2A-B-DCS | ESD 2A status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
215 | ESDI 2A-C-DCS | ESD 2A status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
216 | ESDI 3-A-DCS | ESD 3 status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
217 | ESDI 3-B-DCS | ESD 3 status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
218 | ESDI 3-C-DCS | ESD 3 status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
219 | ESDI 3A-A-DCS | ESD 3A status in DCS (TRAIN A) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
220 | ESDI 3A-B-DCS | ESD 3A status in DCS (TRAIN B) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
221 | ESDI 3A-C-DCS | ESD 3A status in DCS (TRAIN C) | CONTROL ROOM |  | __ |  |  | DO-NIS-R |  | ESD |  | DCS |  | * | * | * | * | * | * | * | * | [5 empty] | X | IF REQUIRED | D02 MODIFIED
D02
D02