## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-TE-PY-0006_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0954 |  |  | Transmital Date: May-15th-2022
Document Title: PAGA Equipment Layout for Area |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-TE-TR-0954 |  |  | Transmital Date: May-15th-2022
[5 empty] | CRS No:NISOC-CRS-BK-GCS-PEDCO-120-TE-PY-0006_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بخش میانی کمپرسورها در ضلع شمالی پوشش صوتی مناسبی ندارد. پیشنهاد میگردد یک عدد پایه به همراه اسپیکر مشابه نمونه های ارایه شده اضافه گردد |  | 1401-2294-96473 | 1401-03-21 | مطابق با نظر کارفرمای محترم یک عدد اسپیکر در قسمت بالای کمپرسور نصب گردید.
2 | بر اساس شرح کار ، جانمایی اسپیکرهای بیرونی می بایست بر اساس مطالعات NOISE STUDY و پوشش مناسب در کلیه محدوده پروژه انجام شود . لذا انجام مطالعات عمومی جهت صحت سنجی پیدمان پیشنهادی الزامی می باشد. |  | 1401-2294-96473 | 1401-03-21 | در شیت سوم و در ویرایش قبلی نیز اضافه شده بود. لازم به توضیح است فلسفه چیدمان بلنگوها تمرکز بر حضور افراد می باشد. در داخل شلتر کمپرسورها بلندگویی جانمایی نشده است. در حالیکه پوشش بلندگوها محوطه شلتر را کاور مینماید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: AP.Golrang | Signature |  |  |  | Clarified By: | Signature
| Date: Jun-08th-2022 |  |  |  |  | Date: