## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-EL-LI-0001-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1320 |  |  | Transmital Date: 27-Aug-2022
Document Title: Electrical Load List - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0106-EL-TR-1320 |  |  | Transmital Date: 27-Aug-2022
[5 empty] | CRS No:NISOC-CRS-BK-W007S-PEDCO-110-EL-LI-0001-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | توان در نظر گرفته شده جهت فیدرهای UPS و شارژر مورد تأیید نیست. مقتضی است محاسبات مربوط به تعییرن آمپر دستگاهههای شارژر سیستم UPS جهت محاسبه توان فیدرهای ورودی سیستم ارائه گردد. |  | 1401-2294-216050 | 1401-06-17 | مطابق با مدرک محاسباتی برای DC Charger و UPS به شماره های "BK-W007S-PEDCO-110-EL-CN-0001" و "BK-W007S-PEDCO-110-EL-CN-0002" که به ترتیب ظرفیت شارژرهای آن برابر 125 آمپر و 120 آمپر می باشد، ولتاژ و بازدهی سیستم در نظر گرفته شده است. از اینرو برای DC Charger توان برابر است با: (125*24) /0.9=3.4 کیلووات و برای AC UPS برابر است با(120*110)/0.9=14.7 کیلووات. این اعداد در مدرک تک خطی منیفولد با شماره ترنسمیتال 1424 نیز درج شده است و در این مدرک هم لحاظ گردیده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 07-Sep-22 |  |  |  |  | Date: