## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-IN-DT-0008_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0797 |  |  | Transmital Date: 10 Apr 2022
Document Title: Data Sheets For Level Switch |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-IN-TR-0797 |  |  | Transmital Date: 10 Apr 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-DT-0008_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comments
1 | با توجه به اينكه مدارك پيش نياز مانند P&ID و Index بعضا ارائه نشده يا نهايي نشده است. مسئوليت تعداد ادوات بر عهده پيمانكار (هيرگان) بوده و در طول مهندسي تفصيلي نهايي خواهد شد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | این مدرک با توجه به آخرین نسخه مدرک I.O LIST و P&ID تهیه شده است. بدیهی است تغییرات آینده روی مدارک پایه، در همه مدارک لحاظ و به روز خواهند شد.
2 | موارد PURCHASING DATA به will be finalized later تغيير پيدا كند. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | اعمال شد.
3 | آيتم هاي Connection Size & Location Upper Connection Size & Location Lower اصلاح گردد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | نحوه نصب این Level Switch ها در یک نقطه هست. این آیتم در دیتا شیت اصلاح شد.
4 | در مورد متريال Float Material شفاف سازي صورت پذيرد... كدام آيتم در نظر گرفته شده است؟ |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | متریال Float Material طبق مدرک Specification for Instrumentation از نوع SS316 هست. در دیتا شیت اصلاح شد.
5 | متريال Flange مشخص شود. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | انجام شد.
6 | بر اساس مدرك specification: Internal stilling well should be supplied by the Vendor, and should have an inside diameter of at least 25mm larger than the displacer or float diameter. The stilling well shall be open at the -bottom end, and should have a vent hole located above the maximum level. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | طبق نظر کارفرمای محترم، این مورد در NOTE 10 صفحه General Note اضافه شد.
Safety & Fire Fighting Comments
7 | سيال Upper نادرست معرفي شده است. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | اصلاح شد.
8 | فشار طراحي صحيح نمي باشد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | اصلاح شد.
9 | رنج فشار عملياتي مورد بازنگري قرار گيرد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | اصلاح شد.
10 | ارتفاع مخزن در مدرك مشخص گردد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | انجام شد.
11 | نوت 1 داراي ابهام مي باشد! |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | اصلاح شد.
12 | مطابق صفحه 5 مدرك؛ دانسيته Upper مشخص گردد. |  | BK-SUR-ENG-INS-01-04115 | 2022-05-01 | اصلاح شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 1 May 2022 |  |  |  |  | Date: