## Calculation
Camp Earthing Calculation |  |  |  | Selection of an earthing conductor for main earthing loop at site
|  | ρ | 60
|  | L (m) | 105
|  | h (m) | 0.6
|  | d (m) | 0.0094407
|  | k | 1.83
|  | Rt | 1.2621
|  | L (m) | 105
|  | S (m)=d | 50
|  | F | 0.59795
Bare Condutor Earth Resistance
| Rn | 0.75466