## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-EL-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1021 |  |  | Transmital Date: 29-May-2022
Document Title: Earthing & Lightning Layout For Camp Area |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1021 |  |  | Transmital Date: 29-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-220-EL-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | کابل رینگ اصلی شبکه ارت از نوع Bare (بدون عایق) باشد. |  | 1401-2294-111529 | 1401-03-31 | محاسبات سیستم زمین توسط هادی لخت به همراه نقشه جانمایی پیوست گردیده است.
2 | تعداد میله های مسی پس از ارائه محاسبات ارت جهت رسیدن مقاومت شبکه ارت به زیر یک اهم اصلاح گردد. |  | 1401-2294-111529 | 1401-03-31 | همانطور که در محاسبات نشان داده شده است، سیستم زمین از طریق قراردادن هادی لخت ایجاد شده است و فقط نقطه نوترال دیزل و ترانسفورماتور به زمین از طریق میله راد متصل شده اند.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 11-Jun-22 |  |  |  |  | Date: