## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-EL-PY-0002_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1021 |  |  | Transmital Date: 29-May-2022
Document Title: Earthing & Lightning Layout For Camp Area |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-EL-TR-1021 |  |  | Transmital Date: 29-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-220-EL-PY-0002_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | According to scope of work, lightning system shall be designed for all buildings in camp area. It shall be rechecked and modified. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | با توجه به اینکه ارتفاع تجهیزات داخل کمپ پایین است، لذا نیازی به در نظر گرفتن سیستم صاعقه گیر نمی باشد.
2 | Earthing cable/Earth pit for pole mounted transformer shall be shown in layout. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | ترانسفورماتور قدرت و دیزل ژنراتور توسط میله راد به زمین متصل شده اند.
3 | Welding socket and outdoor area panels shall be shown and earthed in layout. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | تابلوهای بیرونی به شبکه ارت متصل شدند.
4 | Earth bar shall be connected to main earthing loop from two points instead of one point. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | ارت بارها از دو نقطه متصل شده اند.
5 | Some lighting poles are far from main earthing loop, so it is necessary to considered eath branch from main earthing loop and then above mentioned pole connected to earth branch. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | در نظر گرفته شده است.
6 | Fence of NISOC buildings shall be connected to main earthing loop. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | تمامنی فنس ها به سیستم ارت متصل شدند.
7 | A seperat loop around generator buidling shall be considered and connected to main earthing loop from two points. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | ارت مجزا دورتادور محل دیزل و ترانسفورماتور قرار گرفته است.
8 | In case of the cross between earthing cables and road, the earthing cables shall be laid in conduit for example in front of entrace doors. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | موارد اجرایی در محل سایت توسط پیمانکار در نظر گرفته خواهد شد.
9 | Typical installation detial No. shall be added on layout base on Typical Installation Details & Notes For Earthing and Lightning Protection System. |  | BK-SUR-ENG-ELE-01-04636 | 2022-06-11 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 11-Jun-22 |  |  |  |  | Date: