## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-IN-LI-0007_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0852 |  |  | Transmital Date: 20 APR 2022
Document Title: I&C Power consumption summary - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0008-IN-TR-0852 |  |  | Transmital Date: 20 APR 2022
[5 empty] | CRS No:PEDCO-CRS-BK-W007S-PEDCO-110-IN-LI-0007_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | تخمین بار مصرفی از روی سیستم های موجود برای سیستم جدید، قابل قبول نیست. چرا که سیستم موجود و جدید مشابه نیستند و نمیتواند مبنایی برای طراحی سیستم جدید باشد. تعداد پانل ها و ایستگاههای کاری و سیستم کنترل پکیج ها نامشخص و در مدرک ذکر شده ، تعداد آنها با توجه به کالاهای موجود مشخص میگردد. با توجه به اینکه مدرک در مرحله مهندسی تفصیلی میباشد لازم است ابتدا تعداد و نوع سیستمهای کنترل /پکیج ها/ایستگاههای کاری مشخص، سپس بر اساس تعداد ورودی/خروجی هر سیستم کنترل پکیج اقدام به محاسبه بار مصرفی شود. به دلایل گفته شده این ویرایش مورد تایید نیست. |  | 1401/2294/47232 | 1401/02/11 | بار مصرفی مطابق آخرین طراحی سیستمهای جدیدو همچنین طبق اخرین توافقات در جلسه برگزارشده همزمان با جلسه HAZOP پروژه، در مدرک اعلام شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | پ |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 16 Nov 2021 |  |  |  |  | Date: