## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0002-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1038 |  |  | Transmital Date: 06/June/2022
Document Title: HVAC Calculation Note For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-1038 |  |  | Transmital Date: 06/June/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-HV-CN-0002-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | مطابق اسناد پیمان محاسبات می‌بایست برای ساختمان جدید و ساختمان توسعه ای ضورت پذیرد.که در فایل محاسباتی ارسالی برخی فضاها در محاسبات در نظر گرفته نشده است.(بعنوان مثال اتاق باتری در محاسبات لحاظ نگردیده است.) لازم کلیه فضاها در محاسبات لحاظ و مدرک جهت بررسی مجدد ارسال گردد. |  | 01/2294/96491 | 1401/03/21 | محاسبات بصورت کلی و برای ساختمان جدید و توسعه ای انجام گرفته است. لازم به توضیح است که فضاهایی که از لحاظ دمایی کنترل نمی شوند برای آنها محاسبات بار سرمایشی و گرمایشی انجام نمی شود.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 06/29/2022 |  |  |  |  | Date: 21/09/2022