## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-HV-CN-0002-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1038 |  |  | Transmital Date: 06/June/2022
Document Title: HVAC Calculation Note For Extension of Existing Elect. Building |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-HV-TR-1038 |  |  | Transmital Date: 06/June/2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-HV-CN-0002-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | refer to owner letter number 01/2294/27253 dated 1401/01/28 ,for select of design wet bulb temperature based on MPO (Management and Planning Organization of Iran) published no.271 , if wet bulb shall change then calculation loads and equipment scheduel table for split unit must change consequently. this is for your reply and action (if it is required) |  | BK-SUR-ENG-HVC-01-04923 | 2022-06-29 | according to MPO, published no. 271, wet bulb temperature has changed to 30.5 ◦c .
2 | u-value for metal door is 5.8 w/m2.k and 4w/m2.k is for wooden door , to modify |  | BK-SUR-ENG-HVC-01-04923 | 2022-06-29 | It has done.
3 | to add calculation for select of exhaust fan and sand trap louvre in both co2 and capacitor rooms |  | BK-SUR-ENG-HVC-01-04923 | 2022-06-29 | It has added.
4
5
6
7
8
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 06/29/2022 |  |  |  |  | Date: 21/09/2022