## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W046S-PEDCO-110-HV-CN-0001-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0731 |  |  | Transmital Date: 14/MAR/2022
Document Title:HVAC Calculation Note For Switchgear Building - W046S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-HV-TR-0731 |  |  | Transmital Date: 14/MAR/2022
[5 empty] | CRS No: PEDCO-CRS-BK-W046S-PEDCO-110-HV-CN-0001-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | U-Value for slab on grade shall correct to 2 |  | BK-SUR-ENG-HVC-01-03861 | 2022-04-11 | DONE.
2 | U-Value for Steel Door shall correct to 5.8 |  | BK-SUR-ENG-HVC-01-03861 | 2022-04-11 | DONE.
3 | to explain reason why for roof and external walls insulation has not considered. |  | BK-SUR-ENG-HVC-01-03861 | 2022-04-11 | it has considered.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 5/7/2022 |  |  |  |  | 24/09 /2022