## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W046S-PEDCO-110-HV-PY-0001-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0846 |  |  | Transmital Date: 19/Apr/2022
Document Title:HVAC System Layout For Switchgear Building - W046S |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-HV-TR-0846 |  |  | Transmital Date: 19/Apr/2022
[5 empty] | CRS No: PEDCO-CRS-BK-W046S-PEDCO-110-HV-PY-0001-D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Refer to Letter number 01/2294/27253 dated 1401/1/28 , outdoor wet bulb temperature for HVAC design calculation shall be based on Iranaian Plan and Budget Organization and Publication Code 271, therefore all load calculations reports shall modify and equipment schedule table on this drawing also shall modify too. |  | BK-SUR-ENG-HVC-01-04149 | 2022-05-07 | IT HAS DONE.
2 | indoor temperature for battery room shall condition (T=250C) |  | BK-SUR-ENG-HVC-01-04149 | 2022-05-07 | According to the design criteria doc. The indoor design temperature of This place is not controled. And too client has no comment about battery room control temprature. this item will be cost impact because air chang is 10 and ambient humidity is high.
3 | exhaust fan for battery room shall be had 100 % redundancy unit (it means that , two exhaust fan unit shall consider) |  | BK-SUR-ENG-HVC-01-04149 | 2022-05-07 | this item has been not raised by client, and client has not any comment
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.naserizadeh |  |  | Clarified By: H.ADINEH | Signature
| Date: 5/7/2022 |  |  |  |  | Date: 24/09/2022